## 119_214
S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV)
Slow Speed (TCC 119-2-1-4) | [9 empty] | Slow Speed (TCC 119-2-1-4) | [9 empty] | Slow Speed (TCC 119-2-1-4) | [9 empty] | Slow Speed (TCC 119-2-1-4)
Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015904 | 29999.2 | 0.015904 | 29999.2 | 0.016 | 29999.2 | 0.016 | 29999.2 | 0.016209 | 29999.2 | 0.016405 | 29999.2 | 0.017402 | 29999.2 | 0.018004 | 29999.2 | 0.018203 | 29999.2 | 0.018908 | 29999.2 | 0.020299 | 29999.2 | 0.026886 | 29999.2 | 0.030526 | 29999.2 | 0.036693 | 29999.2 | 0.043886 | 29999.2 | 0.057719
23859.2 | 0.016888 | 23223.6 | 0.016989 | 26793.8 | 0.016405 | 27036 | 0.016307 | 23293.4 | 0.017092 | 22672.9 | 0.017402 | 27225.9 | 0.016504 | 27665.1 | 0.016603 | 27417.2 | 0.016888 | 27144.4 | 0.018004 | 26106.1 | 0.018908 | 28167.5 | 0.018701 | 25334.6 | 0.020503 | 24292.6 | 0.022979 | 29141.7 | 0.027401 | 28650.5 | 0.031487 | 26132.2 | 0.042081 | 25359.9 | 0.053388 | 28707.8 | 0.061227
18341.6 | 0.018203 | 17870.8 | 0.018294 | 20618.1 | 0.017594 | 20804.5 | 0.017594 | 17924.5 | 0.018497 | 17429.6 | 0.018795 | 20929.7 | 0.017896 | 21288.6 | 0.018094 | 21097.8 | 0.018701 | 20867 | 0.019699 | 20088.9 | 0.021191 | 21675.2 | 0.021001 | 19495.2 | 0.023703 | 18674.7 | 0.028011 | 22402.4 | 0.032382 | 26474.2 | 0.033501 | 24099 | 0.045998 | 22380 | 0.062589 | 25589.2 | 0.072211
14114 | 0.019582 | 13751.8 | 0.019699 | 15865.9 | 0.019003 | 15993.3 | 0.019003 | 13779.3 | 0.020097 | 13412.3 | 0.020503 | 16105.6 | 0.019503 | 16381.8 | 0.019897 | 16218.8 | 0.020792 | 16057.4 | 0.022012 | 15458.7 | 0.024498 | 16679.3 | 0.024303 | 14986.8 | 0.028691 | 17238.9 | 0.029922 | 21675.2 | 0.033201 | 24244 | 0.036075 | 22290.7 | 0.050179 | 19032.9 | 0.078696 | 23340 | 0.0824
10860.9 | 0.021107 | 10571.6 | 0.021297 | 12196.7 | 0.020503 | 12307 | 0.020503 | 10603.3 | 0.021815 | 10320.9 | 0.022502 | 12393.5 | 0.021511 | 12593.3 | 0.022211 | 12480.5 | 0.023703 | 12356.3 | 0.025396 | 11883.7 | 0.029594 | 12822.1 | 0.0293 | 14675.3 | 0.029212 | 15708 | 0.032609 | 20088.9 | 0.035325 | 22024.8 | 0.039393 | 20494.8 | 0.055623 | 17050.3 | 0.092999 | 21416.7 | 0.09431
8349.26 | 0.022705 | 8134.98 | 0.022979 | 9385.56 | 0.0221 | 9460.95 | 0.022211 | 8159.42 | 0.023893 | 7934.12 | 0.024993 | 9527.41 | 0.023798 | 9690.76 | 0.025194 | 9603.93 | 0.027594 | 9498.87 | 0.030404 | 11671.7 | 0.030012 | 12593.3 | 0.029802 | 14227.4 | 0.030012 | 14456.9 | 0.035431 | 18068.5 | 0.038613 | 19809.7 | 0.043798 | 19205 | 0.060376 | 14142.3 | 0.12454 | 19651.8 | 0.10783
6424.85 | 0.024498 | 6253.7 | 0.024893 | 7215.08 | 0.023893 | 7280.31 | 0.024206 | 6272.49 | 0.026485 | 6105.4 | 0.028095 | 7331.45 | 0.026886 | 7457.15 | 0.029212 | 7382.95 | 0.033401 | 9162.99 | 0.031299 | 11292.8 | 0.030771 | 12160.2 | 0.030618 | 13793.1 | 0.030771 | 13068 | 0.039511 | 15427.8 | 0.044997 | 17693 | 0.049283 | 17464.5 | 0.068827 | 12356.3 | 0.15612 | 18213.6 | 0.12244
4939.05 | 0.026485 | 4812.29 | 0.026993 | 5552.08 | 0.026013 | 5602.28 | 0.026406 | 4826.75 | 0.029802 | 4698.17 | 0.032382 | 5641.63 | 0.031081 | 5732.62 | 0.035114 | 7265.76 | 0.033906 | 8733.56 | 0.032609 | 10937.2 | 0.031677 | 11706.8 | 0.031582 | 13332 | 0.031804 | 12051.3 | 0.043276 | 12681.8 | 0.056182 | 15897.6 | 0.056069 | 15582.8 | 0.080607 | 11281.5 | 0.18211 | 16762.9 | 0.14041
3800.65 | 0.028806 | 3703.11 | 0.029506 | 4272.39 | 0.028406 | 4306.7 | 0.029212 | 3714.24 | 0.034212 | 3611.68 | 0.038497 | 4336.96 | 0.037099 | 5524.39 | 0.036002 | 6980.86 | 0.034904 | 8241.42 | 0.034315 | 10508.3 | 0.032805 | 11270.3 | 0.032805 | 12732.6 | 0.033201 | 11147 | 0.047636 | 11191.7 | 0.065404 | 14356 | 0.063917 | 14270.1 | 0.09189 | 10372.6 | 0.21179 | 15243.7 | 0.16478
2924.64 | 0.031393 | 2846.74 | 0.032511 | 3284.36 | 0.031299 | 3314.06 | 0.032707 | 2855.29 | 0.040431 | 3533.09 | 0.039118 | 4263.85 | 0.037584 | 5286.59 | 0.037397 | 6640.4 | 0.036474 | 7769.24 | 0.036075 | 9837.21 | 0.034904 | 10850 | 0.033906 | 12184.5 | 0.034695 | 10248.9 | 0.053016 | 9517.88 | 0.08158 | 12796.5 | 0.074933 | 13412.3 | 0.10135 | 9479.89 | 0.24928 | 13655.9 | 0.19946
2248.3 | 0.034625 | 2190.59 | 0.036183 | 2527.35 | 0.035008 | 2550.2 | 0.037285 | 2779.23 | 0.041206 | 3421.82 | 0.040028 | 4113.08 | 0.03869 | 5038.83 | 0.038923 | 6335.53 | 0.038 | 7294.88 | 0.038382 | 9338.75 | 0.036693 | 10414.2 | 0.035325 | 11671.7 | 0.036075 | 9603.93 | 0.057777 | 8526.45 | 0.095927 | 11671.7 | 0.085165 | 12493 | 0.11325 | 8399.5 | 0.31156 | 12605.9 | 0.23012
1730.09 | 0.038497 | 1685.69 | 0.041124 | 1944.83 | 0.039829 | 1960.45 | 0.043798 | 2654.28 | 0.042504 | 3261.45 | 0.041496 | 3955.76 | 0.039908 | 4788.29 | 0.040633 | 5848.43 | 0.040919 | 6856.33 | 0.040919 | 8821.33 | 0.038923 | 10056 | 0.036583 | 11147 | 0.038 | 8733.56 | 0.066194 | 7072.21 | 0.12756 | 10709.9 | 0.097085 | 11452 | 0.13027 | 7577.42 | 0.37751 | 11590.3 | 0.2687
1331.32 | 0.043492 | 1295.86 | 0.047923 | 1495.07 | 0.046413 | 1921.63 | 0.044415 | 2514.75 | 0.044282 | 3074.59 | 0.043492 | 3740.33 | 0.041662 | 4500.43 | 0.042974 | 5496.84 | 0.04358 | 6399.2 | 0.044106 | 8307.62 | 0.041371 | 9642.42 | 0.038191 | 10582.1 | 0.040108 | 7792.59 | 0.077991 | 6179.1 | 0.15911 | 9827.38 | 0.11067 | 10656.5 | 0.14673 | 6680.37 | 0.47751 | 10860.9 | 0.30417
1023.44 | 0.050481 | 1233.89 | 0.049382 | 1456.7 | 0.047304 | 1844.43 | 0.045585 | 2377.79 | 0.046321 | 2912.97 | 0.045494 | 3543.71 | 0.04358 | 4242.59 | 0.045494 | 5171.55 | 0.046321 | 5972.54 | 0.047541 | 7942.06 | 0.043492 | 9199.72 | 0.040108 | 9995.88 | 0.042802 | 7136.15 | 0.089263 | 5641.63 | 0.18504 | 9108.18 | 0.12529 | 9690.76 | 0.17202 | 5984.5 | 0.59028 | 9886.52 | 0.36416
969.646 | 0.052226 | 1144.73 | 0.052018 | 1374.61 | 0.049087 | 1763.27 | 0.047209 | 2225.93 | 0.048989 | 2737.85 | 0.048067 | 3360.78 | 0.045814 | 3983.55 | 0.048356 | 4831.58 | 0.049779 | 5624.73 | 0.05109 | 7397.73 | 0.047304 | 8663.97 | 0.042888 | 9385.56 | 0.046228 | 6707.14 | 0.098849 | 5187.09 | 0.21499 | 8382.72 | 0.14339 | 9044.64 | 0.19395 | 5393.38 | 0.73406 | 8999.53 | 0.44124
886.19 | 0.055401 | 1060.96 | 0.055014 | 1294.56 | 0.051295 | 1668.91 | 0.049185 | 2071.29 | 0.052226 | 2568.12 | 0.050988 | 3174.57 | 0.048163 | 3710.52 | 0.052226 | 4554.76 | 0.053122 | 5281.3 | 0.055235 | 6761.01 | 0.052699 | 8241.42 | 0.045403 | 8847.83 | 0.04958 | 6247.45 | 0.11056 | 4740.64 | 0.25255 | 7623.02 | 0.1676 | 8382.72 | 0.22132 | 4821.92 | 0.93598 | 7957.96 | 0.56827
820.514 | 0.058474 | 975.481 | 0.058709 | 1191.45 | 0.05463 | 1560.76 | 0.05181 | 1944.83 | 0.055345 | 2404.09 | 0.054412 | 3010.7 | 0.050886 | 3470.06 | 0.056069 | 4150.27 | 0.059299 | 4769.17 | 0.062903 | 6303.93 | 0.057661 | 7823.82 | 0.048163 | 8365.97 | 0.053335 | 5726.89 | 0.12769 | 4200.37 | 0.31469 | 6828.96 | 0.20247 | 7823.82 | 0.25104 | 4315.33 | 1.2066 | 7001.84 | 0.76173
765.808 | 0.061719 | 887.076 | 0.063535 | 1100.95 | 0.058067 | 1453.79 | 0.055014 | 1815.16 | 0.05918 | 2241.56 | 0.058416 | 2807.16 | 0.054521 | 3235.47 | 0.060922 | 3831.18 | 0.065404 | 4398.1 | 0.070007 | 5913.12 | 0.062903 | 7442.25 | 0.051295 | 7957.96 | 0.056974 | 5329.05 | 0.14411 | 3789.27 | 0.38092 | 6303.93 | 0.23336 | 7136.15 | 0.29607 | 3967.65 | 1.4916 | 6399.2 | 0.94633
701.297 | 0.066062 | 807.49 | 0.068964 | 974.506 | 0.064689 | 1350.09 | 0.058768 | 1689.06 | 0.063598 | 2100.49 | 0.062589 | 2638.4 | 0.058183 | 2971.82 | 0.067262 | 3582.9 | 0.071421 | 4027.61 | 0.079487 | 5602.28 | 0.067666 | 6959.95 | 0.055901 | 7517.04 | 0.061719 | 4846.09 | 0.16946 | 3340.68 | 0.48087 | 5796.03 | 0.27194 | 6528.47 | 0.34918 | 3611.68 | 1.9019 | 5866 | 1.1698
634.559 | 0.072139 | 744.662 | 0.074559 | 854 | 0.073156 | 1267.66 | 0.062339 | 1557.64 | 0.069379 | 1937.06 | 0.06862 | 2411.32 | 0.064302 | 2743.33 | 0.074634 | 3314.06 | 0.079169 | 3714.24 | 0.089442 | 5286.59 | 0.073302 | 6528.47 | 0.060922 | 7171.92 | 0.065798 | 4522.99 | 0.19125 | 2992.69 | 0.59383 | 5431.27 | 0.30723 | 6068.87 | 0.39965 | 3334 | 2.3699 | 5387.99 | 1.4548
573.026 | 0.079328 | 686.037 | 0.081011 | 761.988 | 0.082648 | 1170.2 | 0.067396 | 1433.58 | 0.075989 | 1786.35 | 0.075459 | 2219.26 | 0.070923 | 2547.65 | 0.081989 | 3099.29 | 0.087146 | 3397.95 | 0.10257 | 4948.94 | 0.080769 | 6172.93 | 0.065864 | 6693.74 | 0.072645 | 4191.98 | 0.21868 | 2697.09 | 0.73701 | 4943.99 | 0.36745 | 5704.03 | 0.45106 | 3111.71 | 2.9149 | 5023.73 | 1.7662
509.755 | 0.088996 | 637.74 | 0.087321 | 692.931 | 0.091798 | 1085.64 | 0.072718 | 1316.76 | 0.084233 | 1662.25 | 0.082731 | 2075.44 | 0.07706 | 2326.05 | 0.092906 | 2878.22 | 0.096698 | 3102.39 | 0.11834 | 4698.17 | 0.087234 | 5726.89 | 0.073229 | 6335.53 | 0.079011 | 3912.49 | 0.24829 | 2411.32 | 0.93973 | 4500.43 | 0.44479 | 5318.4 | 0.51884 | 2921.72 | 3.6105 | 4642.13 | 2.2498
457.113 | 0.10034 | 586.358 | 0.096119 | 625.112 | 0.10381 | 983.316 | 0.081011 | 1209.46 | 0.093559 | 1559.2 | 0.089711 | 1898.71 | 0.086452 | 2121.6 | 0.1057 | 2565.55 | 0.11496 | 2861 | 0.13531 | 4442.3 | 0.094973 | 5371.85 | 0.080607 | 5966.57 | 0.086366 | 3568.6 | 0.29342 | 2157.98 | 1.2103 | 3979.57 | 0.57169 | 4889.91 | 0.61683 | 2740.59 | 4.6732 | 4306.7 | 2.883
412.374 | 0.11314 | 535.891 | 0.10708 | 561.118 | 0.11894 | 892.415 | 0.090885 | 1129.95 | 0.10237 | 1456.7 | 0.098159 | 1735.29 | 0.09767 | 1942.88 | 0.12098 | 2363.57 | 0.13066 | 2654.28 | 0.15333 | 4238.35 | 0.10237 | 5130.35 | 0.086279 | 5619.11 | 0.094688 | 3264.72 | 0.34675 | 1984.11 | 1.4946 | 3501.44 | 0.76479 | 4513.95 | 0.72894 | 2588.74 | 5.9765 | 3963.68 | 3.9584
362.104 | 0.1329 | 496.673 | 0.11764 | 507.721 | 0.1364 | 793.879 | 0.10486 | 1038.91 | 0.11496 | 1359.57 | 0.10773 | 1598.67 | 0.10935 | 1773.89 | 0.13902 | 2162.3 | 0.1506 | 2472.36 | 0.17271 | 4039.71 | 0.11056 | 4793.08 | 0.095736 | 5297.17 | 0.10361 | 3034.88 | 0.39726 | 1806.1 | 1.9057 | 3200.07 | 0.95013 | 4171.07 | 0.86662 | 2487.24 | 7.2271 | 3703.11 | 5.6567
330.277 | 0.15029 | 456.656 | 0.13105 | 474.343 | 0.14999 | 731.378 | 0.11717 | 967.708 | 0.12692 | 1256.3 | 0.12001 | 1466.93 | 0.12404 | 1627.71 | 0.15847 | 1988.09 | 0.17253 | 2323.73 | 0.19202 | 3835.01 | 0.11965 | 4568.45 | 0.10329 | 5079.3 | 0.11112 | 2852.43 | 0.44881 | 1667.24 | 2.3723 | 2933.43 | 1.1733 | 3896.87 | 1.0109 | 2361.21 | 9.6586 | 3536.63 | 7.79
293.222 | 0.17779 | 416.935 | 0.14865 | 440.95 | 0.16643 | 673.798 | 0.13158 | 901.384 | 0.14069 | 1162.03 | 0.13545 | 1384.27 | 0.13586 | 1504.07 | 0.18066 | 1826.08 | 0.19866 | 2166.63 | 0.21759 | 3618.91 | 0.13184 | 4302.4 | 0.11359 | 4860.65 | 0.11941 | 2659.59 | 0.51625 | 1556.08 | 2.9178 | 2694.39 | 1.4591 | 3526.03 | 1.28 | 2273.16 | 12.4889 | 3408.16 | 10.0829
253.898 | 0.21955 | 379.909 | 0.17014 | 400.187 | 0.1924 | 615.805 | 0.14924 | 838.765 | 0.15674 | 1080.23 | 0.1509 | 1297.15 | 0.14999 | 1391.21 | 0.2045 | 1716.3 | 0.22087 | 2038.42 | 0.24386 | 3425.24 | 0.14455 | 4137.84 | 0.12122 | 4660.73 | 0.1282 | 2445.31 | 0.61375 | 1461.07 | 3.6141 | 2512.24 | 1.7697 | 3294.23 | 1.5232 | 2190.59 | 16.5245 | 3281.08 | 12.9079
221.613 | 0.27249 | 345.133 | 0.19531 | 363.919 | 0.22265 | 554.979 | 0.17427 | 772.731 | 0.17743 | 1008.2 | 0.16844 | 1219.17 | 0.1656 | 1279.12 | 0.23642 | 1568.58 | 0.25816 | 1893.02 | 0.27716 | 3225.77 | 0.15991 | 3951.81 | 0.13053 | 4285.22 | 0.14747 | 2257.31 | 0.72603 | 1370.49 | 4.6779 | 2321.41 | 2.2543 | 3127.31 | 1.7539 | 2136.51 | 21.7116 | 3161.9 | 17.1473
199.923 | 0.32169 | 316.06 | 0.22399 | 334.264 | 0.25534 | 506.706 | 0.20066 | 721.932 | 0.19826 | 926.979 | 0.1924 | 1144.73 | 0.1832 | 1179.6 | 0.2714 | 1478.71 | 0.28675 | 1773.89 | 0.31344 | 3074.59 | 0.17357 | 3766.6 | 0.14154 | 4100.76 | 0.15927 | 2085.84 | 0.86402 | 1294.56 | 5.9825 | 2153.67 | 2.8888 | 2989.7 | 1.9854 | 2081.67 | 27.5457 | 3044 | 23.4729
178.561 | 0.39017 | 290.886 | 0.25534 | 305.494 | 0.29577 | 450.308 | 0.24192 | 668.43 | 0.22511 | 817.238 | 0.23665 | 1068.41 | 0.20512 | 1094.36 | 0.30877 | 1402.38 | 0.31627 | 1660.59 | 0.35411 | 2924.64 | 0.18897 | 3526.03 | 0.15879 | 3877.43 | 0.17427 | 1948.72 | 1.0089 | 1243.8 | 7.2271 | 1982.13 | 3.9624 | 2826.88 | 2.344 | 2026.22 | 35.6178 | 2918.8 | 32.6174
163.029 | 0.45559 | 266.382 | 0.29548 | 280.881 | 0.34193 | 406.235 | 0.28732 | 623.24 | 0.25229 | 735.044 | 0.28389 | 984.3 | 0.23571 | 1021.4 | 0.34848 | 1303.65 | 0.36126 | 1551.42 | 0.40326 | 2754.33 | 0.21031 | 3310.74 | 0.17743 | 3669.93 | 0.19106 | 1763.27 | 1.2787 | 1180.78 | 9.6682 | 1851.83 | 5.668 | 2635.76 | 2.912 | 1986.1 | 45.8717 | 2826.88 | 41.8398
150.194 | 0.52668 | 247.381 | 0.33415 | 258.509 | 0.39292 | 379.529 | 0.3233 | 575.898 | 0.28818 | 668.43 | 0.33415 | 924.202 | 0.26259 | 952.348 | 0.39528 | 1217.95 | 0.41141 | 1465.46 | 0.45061 | 2586.16 | 0.23524 | 3136.71 | 0.19512 | 3435.54 | 0.21456 | 1647.36 | 1.5202 | 1136.75 | 12.5014 | 1768.57 | 7.79 | 2512.24 | 3.4724 | 1940.94 | 60.0903 | 2735.11 | 54.6445
139.76 | 0.6016 | 226.996 | 0.38629 | 238.873 | 0.45151 | 340.335 | 0.39017 | 541.277 | 0.32073 | 605.425 | 0.39766 | 860.859 | 0.29726 | 888.852 | 0.44791 | 1129.95 | 0.47513 | 1382.89 | 0.50552 | 2430.68 | 0.26311 | 2936.37 | 0.21911 | 3219.33 | 0.24143 | 1563.88 | 1.7504 | 1095.46 | 16.5245 | 1704.33 | 10.093 | 2394.5 | 4.1614 | 1898.71 | 78.402 | 2670.25 | 68.7068
121.259 | 0.77868 | 207.666 | 0.45016 | 224.288 | 0.50653 | 309.182 | 0.46294 | 502.669 | 0.36489 | 549.457 | 0.47513 | 803.463 | 0.33549 | 824.627 | 0.51163 | 1054.61 | 0.54218 | 1319.39 | 0.55313 | 2268.62 | 0.29875 | 2729.65 | 0.25003 | 3040.96 | 0.26843 | 1495.07 | 1.9834 | 1068.41 | 21.7116 | 1640.78 | 12.9208 | 2291.42 | 4.9523 | 1861.11 | 101.783 | 2606.93 | 86.6476
107.87 | 0.97029 | 189.224 | 0.52932 | 210.594 | 0.56543 | 288.28 | 0.52563 | 465.881 | 0.41805 | 500.662 | 0.56374 | 749.893 | 0.38092 | 765.808 | 0.58969 | 969.646 | 0.6388 | 1255.05 | 0.61498 | 2173.14 | 0.32233 | 2593.93 | 0.2744 | 2883.98 | 0.29577 | 1413.65 | 2.3393 | 1040.99 | 27.5457 | 1581.18 | 17.1473 | 2208.19 | 5.8348 | 1826.08 | 126.576 | 2527.35 | 112.6
97.5079 | 1.1757 | 165.825 | 0.68034 | 196.946 | 0.63562 | 270.408 | 0.58851 | 430.063 | 0.48328 | 460.324 | 0.65367 | 702.701 | 0.4282 | 723.377 | 0.65367 | 915.922 | 0.71953 | 1191.45 | 0.68375 | 2014.1 | 0.36893 | 2425.83 | 0.31063 | 2718.75 | 0.33083 | 1318.07 | 2.9091 | 1013.26 | 35.6178 | 1522.22 | 23.4494 | 2132.24 | 6.8953 | 1782.78 | 168.823 | 2472.36 | 137.393
89.2939 | 1.4061 | 148.403 | 0.83264 | 178.919 | 0.75945 | 254.915 | 0.65236 | 398.191 | 0.55479 | 420.705 | 0.77016 | 640.296 | 0.50958 | 675.823 | 0.7407 | 854.854 | 0.82931 | 1139.02 | 0.75039 | 1904.41 | 0.40977 | 2234.85 | 0.36126 | 2562.99 | 0.36966 | 1256.3 | 3.4724 | 993.199 | 45.8717 | 1459.61 | 32.6174 | 2069.22 | 8.0112 | 1742.24 | 218.077 | 2416.14 | 172.578
81.3641 | 1.6919 | 134.684 | 1.0018 | 166.489 | 0.87009 | 236.496 | 0.7474 | 368.312 | 0.63689 | 387.583 | 0.89838 | 582.268 | 0.6113 | 622.617 | 0.86835 | 803.463 | 0.94633 | 1092.18 | 0.82106 | 1804.3 | 0.45468 | 2090.02 | 0.40936 | 2425.83 | 0.41059 | 1197.42 | 4.1614 | 970.616 | 60.0903 | 1413.65 | 41.8398 | 1992.07 | 9.8143 | 1700.93 | 290.572 | 2370.67 | 205.994
75.1837 | 1.9974 | 122.233 | 1.2151 | 155.856 | 0.99187 | 222.278 | 0.84269 | 325.685 | 0.804 | 362.104 | 1.0221 | 532.153 | 0.72967 | 583.434 | 0.98004 | 743.918 | 1.1161 | 1034.76 | 0.92205 | 1707.74 | 0.50502 | 1974.22 | 0.45696 | 2296.01 | 0.45833 | 1145.88 | 4.9473 | 949.496 | 78.4804 | 1367.76 | 54.5898 | 1923.55 | 12.1441 | 1665.58 | 378.362 | 2316.77 | 253.877
70.2411 | 2.3183 | 110.822 | 1.4886 | 145.464 | 1.1398 | 206.217 | 0.97223 | 297.654 | 0.95203 | 337.961 | 1.171 | 497.667 | 0.83514 | 551.108 | 1.0984 | 698.497 | 1.2723 | 989.234 | 1.017 | 1585.93 | 0.58265 | 1861.11 | 0.51111 | 2166.63 | 0.51419 | 1104.26 | 5.829 | 930.694 | 101.681 | 1335.32 | 68.7068 | 1857.39 | 15.4536 | 1617.97 | 500.122 | 2261.83 | 315.719
66.283 | 2.6587 | 99.9763 | 1.8568 | 134.146 | 1.3469 | 194.402 | 1.0918 | 272.307 | 1.1352 | 314.483 | 1.3523 | 468.217 | 0.94444 | 516.426 | 1.2459 | 649.973 | 1.4797 | 951.396 | 1.1083 | 1490.59 | 0.6576 | 1782.78 | 0.5559 | 2069.22 | 0.56374 | 1066.27 | 6.8884 | 913.178 | 126.703 | 1303.65 | 86.6476 | 1804.3 | 19.2564 | 1601.87 | 588.663 | 2205.98 | 398.558
62.423 | 3.0582 | 93.4974 | 2.1465 | 124.827 | 1.5634 | 183.081 | 1.231 | 252.379 | 1.319 | 292.929 | 1.5665 | 437.874 | 1.0896 | 491.239 | 1.3783 | 610.288 | 1.6919 | 904.092 | 1.2484 | 1423.58 | 0.72025 | 1692.44 | 0.61621 | 1960.45 | 0.62803 | 1034.76 | 8.0112 | 891.523 | 168.823 | 1263.86 | 112.713 | 1740.5 | 25.8897 | 1595.48 | 599.954 | 2149.37 | 501.625
59.1416 | 3.4898 | 87.3509 | 2.5064 | 114.77 | 1.8829 | 173.804 | 1.37 | 235.316 | 1.5232 | 276.146 | 1.7733 | 414.856 | 1.2212 | 468.685 | 1.5202 | 577.629 | 1.9076 | 863.446 | 1.388 | 1346.05 | 0.81289 | 1601.87 | 0.68718 | 1851.83 | 0.70528 | 996.183 | 9.8143 | 871.252 | 218.077 | 1236.36 | 137.393 | 1702.63 | 32.0355 |  |  | 2115.25 | 580.479
55.6974 | 4.0384 | 82.1818 | 2.8917 | 108.519 | 2.1294 | 164.175 | 1.5401 | 222.723 | 1.7157 | 257.735 | 2.0582 | 395.018 | 1.3537 | 444.492 | 1.7089 | 551.66 | 2.1273 | 831.25 | 1.5172 | 1277.84 | 0.90741 | 1534.45 | 0.75114 | 1750.97 | 0.79839 | 961.92 | 12.1319 | 850.591 | 290.572 | 1208.25 | 172.751 | 1650.66 | 41.3407 |  |  | 2104.7 | 599.954
52.1401 | 4.8251 | 77.2413 | 3.3563 | 103.124 | 2.3675 | 155.544 | 1.7295 | 209.334 | 1.9618 | 242.968 | 2.3581 | 372.759 | 1.5401 | 420.284 | 1.9403 | 527.385 | 2.3463 | 800.255 | 1.6717 | 1201.02 | 1.0313 | 1466.93 | 0.82353 | 1682.32 | 0.86835 | 928.835 | 15.4536 | 832.914 | 378.362 | 1185.51 | 205.994 | 1600.27 | 52.8178
49.1528 | 5.7078 | 73.7687 | 3.7805 | 98.3895 | 2.6191 | 147.958 | 1.9268 | 196.749 | 2.2386 | 229.736 | 2.6881 | 355.289 | 1.7174 | 399.387 | 2.1877 | 498.165 | 2.6908 | 757.43 | 1.9229 | 1147.02 | 1.1398 | 1389.82 | 0.91928 | 1600.27 | 0.96738 | 902.285 | 19.2372 | 809.107 | 500.623 | 1158.55 | 253.877 | 1560.76 | 67.279
46.383 | 6.6982 | 69.6814 | 4.4055 | 93.3106 | 2.9708 | 139.76 | 2.1921 | 183.081 | 2.6507 | 219.627 | 3.0067 | 335.268 | 1.9598 | 381.813 | 2.4421 | 471.034 | 3.0705 | 718.331 | 2.2075 | 1084.56 | 1.2915 | 1333.99 | 1.0058 | 1532.92 | 1.0649 | 870.381 | 25.8897 | 801.056 | 588.663 | 1131.08 | 315.719 | 1528.32 | 81.9287
44.1651 | 7.7822 | 66.0845 | 5.0929 | 89.2939 | 3.3262 | 132.414 | 2.4889 | 174.327 | 2.9708 | 207.666 | 3.4689 | 322.445 | 2.1444 | 362.829 | 2.7617 | 446.273 | 3.4828 | 688.098 | 2.4814 | 1036.83 | 1.4274 | 1279.12 | 1.1006 | 1461.07 | 1.191 | 851.442 | 32.0355 | 797.858 | 599.954 | 1103.15 | 398.558 | 1490.59 | 104.464
42.2217 | 8.9071 | 62.548 | 5.9706 | 85.1091 | 3.7654 | 126.714 | 2.77 | 164.339 | 3.4207 | 197.933 | 3.919 | 310.111 | 2.3533 | 344.1 | 3.1735 | 425.784 | 3.9387 | 665.096 | 2.7424 | 991.214 | 1.5838 | 1227.74 | 1.2103 | 1392.6 | 1.3296 | 825.452 | 41.3407 |  |  | 1074.84 | 502.127 | 1461.07 | 131.085
40.6474 | 10.2353 | 59.557 | 7.0065 | 81.8537 | 4.199 | 120.413 | 3.1451 | 155.078 | 3.9703 | 189.792 | 4.4143 | 300.345 | 2.5621 | 328.63 | 3.5961 | 409.088 | 4.3791 | 642.22 | 3.046 | 940.048 | 1.8019 | 1171.37 | 1.3416 | 1332.65 | 1.4812 | 800.255 | 52.8178 |  |  | 1057.78 | 581.06 | 1427.85 | 167.981
39.3279 | 11.8088 | 56.9364 | 8.214 | 78.4086 | 4.7202 | 114.77 | 3.5603 | 148.998 | 4.4408 | 183.265 | 4.8981 | 287.416 | 2.8401 | 313.228 | 4.1076 | 393.441 | 4.8932 | 619.511 | 3.4002 | 894.201 | 2.0316 | 1133.34 | 1.4446 | 1276.56 | 1.6501 | 780.497 | 67.279 |  |  | 1052.5 | 599.954 | 1396.78 | 222.038
37.8236 | 14.4088 | 54.5945 | 9.6296 | 75.5605 | 5.306 | 110.049 | 3.9822 | 144.161 | 4.8688 | 178.204 | 5.338 | 278.643 | 3.0859 | 299.146 | 4.7343 | 378.014 | 5.4895 | 595.22 | 3.9308 | 855.709 | 2.277 | 1092.18 | 1.5775 | 1220.39 | 1.8457 | 764.277 | 82.0107 |  |  |  |  | 1370.49 | 288.545
36.6691 | 17.6872 | 52.6115 | 11.2779 | 73.3274 | 5.9171 | 105.207 | 4.526 | 138.647 | 5.397 | 171.56 | 5.9945 | 268.253 | 3.4104 | 287.992 | 5.3007 | 363.919 | 6.1095 | 578.785 | 4.3572 | 822.979 | 2.524 | 1051.45 | 1.7209 | 1177.24 | 2.0337 | 745.407 | 104.36 |  |  |  |  | 1346.05 | 367.915
35.6566 | 21.8422 | 50.9036 | 13.341 | 70.5932 | 6.8747 | 101.183 | 5.0776 | 133.477 | 5.9885 | 165.99 | 6.6982 | 258.251 | 3.788 | 278.364 | 5.9527 | 351.754 | 6.7656 | 560.557 | 4.9325 | 793.085 | 2.7894 | 1019.36 | 1.8623 | 1126.56 | 2.2952 | 730.647 | 131.085 |  |  |  |  | 1327.33 | 462.595
35.0205 | 26.0195 | 49.6468 | 15.5466 | 68.1652 | 7.9474 | 97.4105 | 5.6964 | 128.243 | 6.7927 | 161.73 | 7.4101 | 249.868 | 4.1614 | 267.717 | 6.7859 | 337.961 | 7.6434 | 545.079 | 5.5226 | 763.514 | 3.1169 | 973.532 | 2.0893 | 1078.07 | 2.5905 | 714.034 | 167.981 |  |  |  |  | 1311.5 | 599.954
34.3271 | 32.65 | 48.3726 | 18.65 | 65.6892 | 9.345 | 94.0601 | 6.4163 | 123.585 | 7.7434 | 156.95 | 8.3632 | 240.791 | 4.6592 | 259.545 | 7.6971 | 328.63 | 8.4896 | 526.858 | 6.4099 | 735.044 | 3.4828 | 942.872 | 2.2701 | 1040.99 | 2.8543 | 698.497 | 222.038
33.816 | 39.3638 | 47.5572 | 21.6899 | 63.5568 | 10.9336 | 91.0068 | 7.1911 | 119.813 | 8.722 | 151.856 | 9.4673 | 233.208 | 5.1441 | 251.371 | 8.9338 | 319.875 | 9.4578 | 510.776 | 7.3805 | 706.223 | 3.9387 | 909.533 | 2.4964 | 1002.17 | 3.2118 | 685.351 | 288.545
33.4461 | 48.4653 | 46.99 | 25.3263 | 62.0496 | 12.4764 | 88.3171 | 8.0917 | 115.808 | 10.225 | 147.81 | 10.8356 | 226.316 | 5.6737 | 244.186 | 10.1944 | 313.541 | 10.3381 | 498.165 | 8.3968 | 682.615 | 4.3879 | 879.128 | 2.7617 | 970.616 | 3.5603 | 673.125 | 367.915
33.2128 | 60.1504 | 46.3367 | 29.7208 | 60.5781 | 14.4811 | 85.8785 | 9.1783 | 112.273 | 11.8679 | 143.873 | 12.4266 | 219.847 | 6.2392 | 239.351 | 11.4598 | 304.884 | 11.8088 | 485.865 | 9.6296 | 659.796 | 4.9374 | 853.146 | 3.0067 | 940.048 | 3.9624 | 663.767 | 462.595
33.0802 | 79.0317 | 45.8298 | 34.7384 | 59.438 | 16.8246 | 83.9259 | 10.39 | 109.173 | 13.6924 | 140.602 | 14.237 | 212.285 | 7.1124 | 233.675 | 12.9597 | 298.847 | 13.1555 | 474.343 | 10.9665 | 635.194 | 5.6908 | 827.932 | 3.2866 | 907.715 | 4.4765 | 655.849 | 572.409
33.0141 | 108.294 | 45.3284 | 40.9293 | 58.5531 | 19.4111 | 81.6085 | 12.0835 | 106.477 | 16.0201 | 136.993 | 16.7407 | 204.779 | 8.0998 | 229.736 | 14.4956 | 292.052 | 14.7884 | 464.486 | 12.3894 | 620.752 | 6.2579 | 803.463 | 3.5889 | 882.652 | 4.9721 | 651.274 | 599.954
33.0141 | 153.216 | 44.9223 | 48.5623 | 57.6814 | 23.2858 | 79.6732 | 14.011 | 104.578 | 18.3173 | 134.012 | 19.4111 | 198.528 | 9.2243 | 225.638 | 16.2135 | 285.411 | 16.8583 | 452.565 | 14.6852 | 603.008 | 7.1124 | 782.06 | 3.8917 | 854 | 5.6454 | 649.323 | 599.954
33.0141 | 221.152 | 44.5643 | 58.724 | 56.9364 | 27.6561 | 77.9396 | 16.0682 | 102.507 | 21.4311 | 130.312 | 23.5434 | 192.276 | 10.6211 | 221.834 | 18.1895 | 279.76 | 19.0648 | 442.275 | 17.2505 | 588.12 | 8.0192 | 763.514 | 4.2412 | 824.627 | 6.5656
33.0141 | 317.619 | 44.3864 | 72.519 | 56.3135 | 33.4097 | 76.856 | 18.135 | 100.477 | 25.1497 | 127.987 | 27.8782 | 187.154 | 12.1198 | 216.574 | 21.3456 | 273.399 | 22.0177 | 433.951 | 19.8429 | 573.026 | 9.1143 | 743.175 | 4.6779 | 803.463 | 7.3953
32.9811 | 467.712 | 44.1651 | 91.6383 | 55.7532 | 40.1189 | 75.4095 | 21.3456 | 98.5864 | 29.1906 | 125.578 | 33.0112 | 182.168 | 14.3513 | 213.136 | 24.8 | 266.648 | 26.0716 | 425.358 | 23.3792 | 561.679 | 10.2969 | 720.49 | 5.248 | 779.717 | 8.4727
32.9481 | 545.582 | 44.1651 | 121.613 | 55.3642 | 49.3949 | 74.1384 | 24.8497 | 97.4105 | 33.6444 | 123.709 | 38.7778 | 178.383 | 16.6239 | 209.334 | 29.5134 | 262.154 | 29.7208 | 417.77 | 27.2989 | 547.811 | 11.7381 | 703.404 | 5.7883 | 757.43 | 9.9627
32.9152 | 599.954 | 44.1651 | 157.095 | 55.1984 | 62.4801 | 73.1809 | 29.074 | 95.8643 | 39.8789 | 122.111 | 45.6885 | 174.501 | 19.2757 | 204.984 | 36.1923 | 257.735 | 34.7037 | 409.907 | 31.8439 | 534.82 | 13.5969 | 686.037 | 6.4292 | 738.729 | 11.4254
|  | 44.1651 | 198.314 | 55.1984 | 81.9287 | 72.0913 | 34.3928 | 94.6261 | 46.7983 | 120.413 | 55.5258 | 170.193 | 23.2858 | 201.126 | 44.073 | 253.644 | 39.3245 | 402.595 | 38.1622 | 523.183 | 15.6402 | 671.109 | 7.1409 | 716.18 | 13.6651
|  | 44.1651 | 274.198 | 55.1984 | 111.146 | 71.1602 | 41.382 | 93.404 | 56.0839 | 119.096 | 65.7493 | 167.491 | 27.7392 | 197.736 | 54.0467 | 249.868 | 45.4152 | 395.018 | 46.1016 | 513.336 | 17.7227 | 655.194 | 8.0353 | 700.596 | 15.829
|  | 44.1651 | 357.041 | 55.1984 | 144.005 | 70.3817 | 50.3424 | 92.6597 | 65.9468 | 117.558 | 81.8468 | 164.668 | 33.2431 | 195.182 | 63.4878 | 246.148 | 54.4808 | 388.748 | 54.2633 | 505.188 | 19.823 | 637.103 | 9.252 | 687.41 | 18.1169
|  | 44.0768 | 437.402 | 55.1984 | 187.889 | 69.5422 | 61.3655 | 91.8295 | 77.312 | 116.155 | 103.218 | 162.379 | 39.9987 | 192.853 | 74.2805 | 242.968 | 63.6149 | 383.343 | 63.2344 | 495.185 | 23.1465 | 620.752 | 10.653 | 667.094 | 22.1502
|  | 44.0328 | 541.776 | 55.1984 | 253.623 | 68.9881 | 73.9101 | 91.0978 | 92.0056 | 115.115 | 126.83 | 160.442 | 47.08 | 190.744 | 87.0819 | 239.59 | 76.3898 | 379.15 | 72.9554 | 487.813 | 26.3336 | 607.852 | 12.1562 | 650.623 | 26.3336
|  | 43.9888 | 599.954 | 55.1984 | 345.451 | 68.3016 | 90.9081 | 90.5529 | 108.728 | 113.514 | 168.149 | 158.528 | 56.365 | 188.28 | 102.498 | 236.26 | 91.6383 | 373.505 | 85.7854 | 479.11 | 30.5647 | 595.816 | 13.8162 | 634.559 | 31.2446
|  |  |  | 55.1984 | 466.777 | 67.8252 | 113.618 | 90.1012 | 131.611 | 112.723 | 205.172 | 156.48 | 67.7516 | 186.78 | 118.019 | 232.742 | 113.732 | 368.681 | 98.7755 | 473.869 | 34.3241 | 582.851 | 16.1004 | 620.752 | 37.2945
|  |  |  | 55.1984 | 566.713 | 67.4195 | 140.731 | 89.7415 | 152.91 | 112.16 | 254.895 | 154.768 | 80.3867 | 185.106 | 136.982 | 229.736 | 135.89 | 364.283 | 113.846 | 466.348 | 40.8067 | 574.173 | 18.0265 | 612.734 | 43.1571
|  |  |  | 55.1432 | 599.954 | 67.0162 | 180.161 | 88.8486 | 188.077 | 111.601 | 314.458 | 152.312 | 103.012 | 183.631 | 161.233 | 227.223 | 161.717 | 360.298 | 133.6 | 459.864 | 46.7516 | 563.931 | 20.7147 | 600.001 | 53.1356
[6 empty] | 66.7486 | 228.572 | 88.5824 | 239.332 | 111.155 | 384.849 | 150.345 | 130.692 | 181.804 | 191.684 | 224.512 | 196.733 | 356 | 157.252 | 453.471 | 55.4149 | 556.091 | 23.426 | 591.068 | 66.7429
[6 empty] | 66.4822 | 295.258 | 88.1406 | 310.086 | 110.49 | 487.287 | 148.254 | 168.991 | 180.356 | 226.75 | 222.278 | 237.425 | 352.811 | 180.883 | 447.167 | 65.8809 | 546.717 | 27.5732 | 582.851 | 79.4278
[6 empty] | 66.283 | 365.714 | 88.0525 | 416.069 | 110.27 | 570.124 | 146.779 | 205.789 | 178.919 | 269.307 | 220.507 | 280.858 | 349.649 | 209.736 | 441.833 | 77.0034 | 538.039 | 32.1961 | 574.173 | 98.1846
[6 empty] | 66.2168 | 452.077 | 88.0525 | 527.872 | 110.049 | 599.954 | 145.464 | 269.307 | 178.026 | 311.329 | 218.75 | 330.581 | 346.17 | 245.145 | 435.255 | 94.4291 | 529.499 | 38.8166 | 568.46 | 116.845
[6 empty] | 66.0845 | 540.153 | 88.0525 | 574.128 |  |  | 144.45 | 324.359 | 176.961 | 372.357 | 217.007 | 414.408 | 343.412 | 286.532 | 430.924 | 109.382 | 522.138 | 45.8717 | 562.804 | 140.449
[6 empty] | 66.0845 | 599.954 | 88.0525 | 599.954 |  |  | 143.585 | 405.797 | 175.903 | 451.625 | 215.925 | 497.131 | 341.358 | 325.985 | 425.784 | 129.004 | 515.909 | 54.3176 | 556.091 | 179.441
[12 empty] | 143.012 | 502.127 | 175.2 | 532.111 | 215.709 | 566.713 | 338.638 | 383.696 | 421.969 | 149.134 | 507.721 | 67.6163 | 551.66 | 217.859
[12 empty] | 142.584 | 572.409 | 174.501 | 573.555 | 215.278 | 599.954 | 336.276 | 445.792 | 417.352 | 173.27 | 501.664 | 79.5073 | 547.811 | 272.558
[12 empty] | 142.584 | 599.954 | 173.978 | 599.954 |  |  | 334.264 | 517.419 | 413.2 | 209.108 | 495.185 | 95.5691 | 542.903 | 340.649
[18 empty] | 332.264 | 570.694 | 408.679 | 255.916 | 490.748 | 111.815 | 540.195 | 435.22
[18 empty] | 331.269 | 599.954 | 405.018 | 300.922 | 483.926 | 144.149 | 538.039 | 523.665
[20 empty] | 401.791 | 362.437 | 479.11 | 177.478 | 536.427 | 580.479
[20 empty] | 399.387 | 422.358 | 474.818 | 218.951 | 535.356 | 599.954
[20 empty] | 397.793 | 485.827 | 469.154 | 289.123
[20 empty] | 396.601 | 568.416 | 466.814 | 370.499
[20 empty] | 395.809 | 599.954 | 464.486 | 465.845
[22 empty] | 463.095 | 576.43
[22 empty] | 462.632 | 599.954