## 119_4
S&C Power Fuses - Type SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Type SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Type SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Type SM-4 and SM-5
Slow Speed (TCC 119-4) | [9 empty] | Slow Speed (TCC 119-4) | [9 empty] | Slow Speed (TCC 119-4) | [9 empty] | Slow Speed (TCC 119-4)
Minimum Melting Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated March 18, 1985
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
887.341 | 0.010031 | 1154.35 | 0.01 | 1420.87 | 0.010031 | 1810.23 | 0.010021 | 2608.62 | 0.01001 | 3282.09 | 0.010031 | 3939.93 | 0.01001 | 5014.36 | 0.01001 | 6341.93 | 0.010021 | 8233.07 | 0.01 | 10240.3 | 0.010031 | 11307.9 | 0.010052 | 12750.2 | 0.010021 | 16295.1 | 0.010052 | 20566.4 | 0.010031 | 25367.8 | 0.010052 | 29452 | 0.010052 | 36594.3 | 0.010042 | 45563.7 | 0.010021
801.89 | 0.012195 | 1073 | 0.011466 | 1186.11 | 0.014263 | 1551.09 | 0.013467 | 2289.5 | 0.013079 | 3050.81 | 0.011611 | 3411.34 | 0.013341 | 4574.25 | 0.011943 | 5560.3 | 0.013079 | 7652.91 | 0.011708 | 9196.4 | 0.012622 | 9966.13 | 0.012943 | 11062.7 | 0.013383 | 13860.8 | 0.013924 | 18012.8 | 0.013299 | 23580.2 | 0.011611 | 26951.2 | 0.011993 | 31552.7 | 0.013608 | 39989.8 | 0.013147
593.672 | 0.022278 | 889.196 | 0.016647 | 937.818 | 0.023011 | 1226.4 | 0.021727 | 1860.04 | 0.019613 | 2504.55 | 0.017285 | 2702.87 | 0.021145 | 3882.77 | 0.01663 | 4583.81 | 0.019409 | 6915.93 | 0.014263 | 7781.8 | 0.017539 | 8494.98 | 0.01765 | 9206.01 | 0.019429 | 11237.3 | 0.021145 | 15131.1 | 0.018889 | 20803.9 | 0.014934 | 22758 | 0.016857 | 27606.2 | 0.017686 | 32624.5 | 0.019778
475.811 | 0.034652 | 706.737 | 0.026302 | 690.691 | 0.04195 | 951.625 | 0.036093 | 1469.14 | 0.031445 | 2082.02 | 0.025095 | 2009.42 | 0.038347 | 3275.25 | 0.02335 | 3755.21 | 0.028534 | 5956.89 | 0.019288 | 6361.82 | 0.025975 | 7025.07 | 0.025866 | 7541.88 | 0.029106 | 8783.55 | 0.034616 | 12395.9 | 0.027945 | 17457.4 | 0.021189 | 18031.6 | 0.026885 | 23335.4 | 0.024912 | 26587.9 | 0.029473
378.177 | 0.054922 | 527.064 | 0.047303 | 530.376 | 0.071383 | 750.85 | 0.057867 | 1126.96 | 0.053451 | 1739.83 | 0.03598 | 1475.28 | 0.071234 | 2722.7 | 0.033583 | 2975.33 | 0.045415 | 5024.84 | 0.027026 | 5316.23 | 0.03728 | 5791.34 | 0.038267 | 6025.69 | 0.045463 | 6879.92 | 0.056434 | 10081.2 | 0.042258 | 14331.6 | 0.031577 | 15210.3 | 0.037909 | 19581.7 | 0.035273 | 22357.7 | 0.041819
306.918 | 0.082967 | 343.188 | 0.11138 | 419.351 | 0.11267 | 568.799 | 0.10033 | 820.519 | 0.10086 | 1365.61 | 0.058413 | 1144.75 | 0.11871 | 2125.95 | 0.055383 | 2294.29 | 0.076556 | 4190.22 | 0.039197 | 4310.01 | 0.057027 | 4656.15 | 0.05915 | 4900.51 | 0.069109 | 5327.34 | 0.093652 | 8130.58 | 0.065183 | 11307.9 | 0.050626 | 12434.8 | 0.056552 | 15226.1 | 0.05823 | 18297.1 | 0.061866
247.531 | 0.12798 | 255.406 | 0.20031 | 321.68 | 0.19112 | 453.502 | 0.15721 | 584.449 | 0.19617 | 1046.45 | 0.097851 | 896.653 | 0.19393 | 1728.97 | 0.08375 | 1842.65 | 0.11896 | 3575.41 | 0.053451 | 3483.31 | 0.086596 | 3723.98 | 0.091525 | 4056.8 | 0.10054 | 4164.06 | 0.15428 | 6640.02 | 0.097749 | 9100.9 | 0.078663 | 10380.2 | 0.081167 | 12750.2 | 0.082967 | 15115.3 | 0.090574
194.899 | 0.20669 | 195.511 | 0.34914 | 252.227 | 0.31782 | 338.916 | 0.28038 | 450.671 | 0.33207 | 826.537 | 0.15836 | 703.792 | 0.31484 | 1302.94 | 0.14613 | 1495.44 | 0.17951 | 3009.69 | 0.075445 | 2771.45 | 0.13654 | 2987.78 | 0.14311 | 3251.4 | 0.15607 | 3414.9 | 0.22848 | 5349.63 | 0.15188 | 7502.61 | 0.11577 | 8156.08 | 0.13191 | 10358.6 | 0.12691 | 12280 | 0.13739
152.023 | 0.34407 | 155.88 | 0.56623 | 194.696 | 0.54819 | 266.019 | 0.46046 | 350.063 | 0.57158 | 613.198 | 0.2878 | 565.838 | 0.49177 | 1026.97 | 0.23575 | 1191.07 | 0.28481 | 2573.46 | 0.10472 | 2261 | 0.20518 | 2347.59 | 0.23209 | 2560.06 | 0.25126 | 2702.87 | 0.36939 | 4323.53 | 0.23331 | 5773.23 | 0.19454 | 6619.26 | 0.19927 | 8389.23 | 0.19171 | 10347.7 | 0.19535
113.138 | 0.64452 | 126.376 | 0.88999 | 152.182 | 0.93184 | 196.329 | 0.85894 | 282.918 | 0.89745 | 453.502 | 0.54477 | 431.339 | 0.87433 | 786.142 | 0.40963 | 922.285 | 0.48312 | 2117.09 | 0.15428 | 1831.14 | 0.31484 | 1856.16 | 0.37601 | 1921.22 | 0.45425 | 1988.55 | 0.69485 | 3422.04 | 0.37996 | 4598.18 | 0.31027 | 5451.1 | 0.29541 | 6894.3 | 0.29021 | 8620.05 | 0.28481
92.5903 | 0.99625 | 104.618 | 1.3458 | 122.48 | 1.5144 | 158.506 | 1.3472 | 238.153 | 1.3098 | 316.352 | 1.1762 | 347.514 | 1.4047 | 629.412 | 0.67131 | 755.567 | 0.73439 | 1783.97 | 0.21663 | 1414.95 | 0.54024 | 1446.31 | 0.63716 | 1522.22 | 0.74133 | 1605.46 | 1.1036 | 2874.58 | 0.55337 | 3739.56 | 0.48261 | 4598.18 | 0.42223 | 5773.23 | 0.4209 | 7128.5 | 0.42399
78.2662 | 1.4464 | 86.9689 | 2.0738 | 100.34 | 2.4229 | 133.565 | 1.9786 | 191.871 | 2.1331 | 251.438 | 1.9683 | 297.145 | 2.0161 | 504.455 | 1.0752 | 599.902 | 1.2073 | 1490.77 | 0.3119 | 1117.59 | 0.90404 | 1124.61 | 1.0979 | 1288.07 | 1.0752 | 1341.59 | 1.6637 | 2372.22 | 0.84471 | 2997.15 | 0.777 | 3882.77 | 0.61109 | 4931.3 | 0.58915 | 6120.79 | 0.59783
68.4055 | 1.9848 | 77.1307 | 2.8073 | 87.2416 | 3.4235 | 119.325 | 2.6094 | 161.344 | 3.2425 | 213.429 | 2.9455 | 259.437 | 2.8309 | 419.351 | 1.6242 | 490.948 | 1.8897 | 1288.07 | 0.42311 | 902.286 | 1.4359 | 917.483 | 1.7528 | 1073 | 1.6123 | 1151.94 | 2.3878 | 1921.22 | 1.35 | 2522.92 | 1.1435 | 3368.87 | 0.82984 | 4216.55 | 0.83593 | 5468.2 | 0.76014
60.5407 | 2.6812 | 68.9072 | 3.757 | 76.4094 | 4.9342 | 108.285 | 3.3075 | 139.697 | 4.7224 | 185.956 | 4.11 | 225.57 | 4.0461 | 341.758 | 2.6067 | 421.106 | 2.7037 | 1085.39 | 0.60664 | 738.413 | 2.3117 | 772.314 | 2.6451 | 930.99 | 2.2782 | 1009.96 | 3.2972 | 1644.47 | 1.9397 | 2128.17 | 1.713 | 2847.7 | 1.1898 | 3681.46 | 1.1269 | 4951.94 | 0.96149
53.7483 | 3.6716 | 61.4962 | 5.1932 | 67.9784 | 7.1487 | 96.1361 | 4.6345 | 121.715 | 7.0892 | 167.348 | 5.4831 | 203.422 | 5.4888 | 296.835 | 3.6986 | 366.517 | 3.7964 | 909.853 | 0.89185 | 656.936 | 3.0583 | 686.379 | 3.5807 | 836.956 | 2.9733 | 896.653 | 4.6929 | 1437.28 | 2.6953 | 1827.32 | 2.5131 | 2455.37 | 1.6654 | 3161.04 | 1.5989 | 4498.48 | 1.2023
48.8265 | 4.8271 | 55.8066 | 7.1115 | 61.3039 | 10.3679 | 87.8815 | 6.0297 | 111.846 | 9.4972 | 147.953 | 7.8943 | 184.217 | 7.4381 | 266.575 | 4.96 | 324.039 | 5.2808 | 782.049 | 1.2367 | 579.588 | 4.2408 | 599.902 | 5.3195 | 743.052 | 4.1143 | 800.217 | 6.6517 | 1241.86 | 3.905 | 1588.78 | 3.7609 | 2146.02 | 2.3117 | 2785.95 | 2.1555 | 4112.22 | 1.5002
45.2439 | 6.074 | 51.389 | 9.7994 | 56.6282 | 15.1156 | 79.2528 | 8.5912 | 102.243 | 13.1279 | 134.545 | 10.7989 | 168.048 | 10.2174 | 241.911 | 6.5757 | 281.739 | 7.9605 | 659.684 | 1.8295 | 504.455 | 6.3265 | 536.501 | 7.5793 | 660.373 | 5.771 | 727.7 | 9.2524 | 1112.93 | 5.2863 | 1429.8 | 5.215 | 1891.37 | 3.1425 | 2496.72 | 2.8457 | 3689.16 | 1.9765
42.1876 | 7.7879 | 47.0256 | 14.5578 | 53.0792 | 23.684 | 72.2968 | 12.5383 | 95.0385 | 17.7716 | 124.024 | 14.4518 | 155.393 | 13.7596 | 215.443 | 9.5869 | 256.743 | 10.8668 | 579.588 | 2.4974 | 452.557 | 8.9952 | 484.836 | 11.1659 | 598.026 | 8.0022 | 675.715 | 12.3563 | 996.354 | 7.3301 | 1301.58 | 7.3072 | 1689.71 | 4.2853 | 2294.29 | 3.5807 | 3397.13 | 2.4844
38.4446 | 11.0846 | 43.8947 | 22.199 | 50.8553 | 39.6745 | 68.1916 | 17.1516 | 88.526 | 25.4803 | 115.284 | 20.1233 | 145.806 | 19.1195 | 197.356 | 13.5316 | 232.989 | 15.9758 | 523.227 | 3.1888 | 419.789 | 12.0379 | 445.991 | 15.7275 | 542.131 | 11.7767 | 636.017 | 16.6922 | 904.172 | 10.2816 | 1199.8 | 10.4658 | 1517.46 | 5.7649 | 2177.61 | 4.1402 | 3115.18 | 3.1656
35.5495 | 16.0931 | 41.968 | 30.9109 | 49.6488 | 95.5886 | 64.9944 | 24.9796 | 84.1117 | 37.9719 | 107.609 | 30.1458 | 136.526 | 31.7286 | 182.875 | 19.1195 | 218.615 | 21.627 | 458.74 | 4.515 | 390.208 | 16.8851 | 421.106 | 21.3353 | 507.095 | 16.5533 | 604.302 | 22.526 | 834.339 | 14.2569 | 1134.04 | 14.2867 | 1420.87 | 7.2691 | 1998.96 | 5.2478 | 2838.79 | 4.2764
33.5659 | 24.1082 | 40.4623 | 50.2885 | 49.4936 | 231.751 | 62.1415 | 38.4106 | 81.2635 | 58.3276 | 102.778 | 47.1356 | 131.49 | 53.5965 | 173.213 | 26.2363 | 207.714 | 30.6858 | 411.115 | 6.2086 | 370.75 | 22.6913 | 400.107 | 33.3596 | 479.3 | 25.4006 | 579.588 | 32.4321 | 792.734 | 18.6267 | 1073 | 20.8289 | 1302.94 | 9.9126 | 1877.6 | 6.3596 | 2597.75 | 5.7589
32.2605 | 38.0911 | 39.5849 | 93.9065 | 49.4936 | 455.959 | 60.0372 | 66.9489 | 79.4184 | 98.8371 | 99.6095 | 77.6513 | 128.103 | 107.674 | 164.576 | 40.0492 | 200.68 | 44.042 | 370.363 | 8.8 | 353.367 | 33.7099 | 386.559 | 50.4464 | 456.829 | 42.108 | 557.629 | 52.4886 | 751.634 | 26.9304 | 1029.12 | 29.155 | 1216.2 | 13.5599 | 1750.76 | 8.1968 | 2424.8 | 7.2616
31.1031 | 72.9349 | 39.5024 | 196.704 | 49.4936 | 597.581 | 59.4138 | 171.194 | 78.6758 | 212.73 | 98.2668 | 174.261 | 127.436 | 226.014 | 159.835 | 63.5427 | 197.769 | 70.0239 | 340.334 | 12.486 | 341.045 | 56.1167 | 380.95 | 84.2415 | 441.82 | 73.7776 | 542.131 | 91.2003 | 722.401 | 38.9764 | 991.167 | 42.9519 | 1148.34 | 18.6657 | 1603.78 | 11.2596 | 2277.58 | 9.3789
30.2387 | 151.662 | 39.42 | 377.426 |  |  | 59.3518 | 392.296 | 78.8402 | 447.467 | 98.5751 | 374.677 | 127.17 | 379.006 | 157.516 | 122.945 | 197.769 | 121.161 | 317.675 | 18.3181 | 331.913 | 95.3892 | 378.967 | 161.469 | 434.049 | 138.49 | 538.184 | 154.863 | 694.306 | 60.8158 | 959.605 | 63.0799 | 1088.8 | 26.5118 | 1487.66 | 15.8099 | 2154.99 | 12.2152
29.8 | 353.393 | 39.5024 | 597.581 |  |  | 59.4138 | 598.205 | 78.758 | 598.83 | 98.2668 | 598.205 | 127.569 | 596.957 | 157.352 | 235.41 | 196.534 | 225.072 | 303.731 | 24.9796 | 330.185 | 169.062 | 378.967 | 314.055 | 430.889 | 258.339 | 536.501 | 273.042 | 675.01 | 101.769 | 927.111 | 108.237 | 1035.59 | 38.2905 | 1414.95 | 20.2287 | 2051.82 | 16.2281
29.6448 | 597.581 | [12 empty] | 156.696 | 438.218 | 195.919 | 433.213 | 291.918 | 37.8136 | 329.153 | 321.69 | 376.601 | 504.569 | 430.889 | 419.412 | 536.501 | 468.02 | 655.565 | 224.368 | 893.849 | 209.643 | 1005.75 | 55.708 | 1326.27 | 28.8521 | 1935.31 | 23.4624
[14 empty] | 156.86 | 597.581 | 196.534 | 600.082 | 282.328 | 58.6942 | 328.467 | 601.965 | 376.601 | 601.337 | 430.889 | 601.965 | 537.623 | 601.965 | 646.054 | 458.825 | 874.467 | 357.476 | 981.899 | 88.0188 | 1269.38 | 42.4613 | 1844.57 | 34.7102
[18 empty] | 273.909 | 115.478 | [8 empty] | 642.02 | 599.456 | 864.483 | 532.172 | 972.717 | 151.346 | 1230.24 | 62.8169 | 1772.83 | 50.9759
[18 empty] | 271.065 | 195.067 | [10 empty] | 858.189 | 601.965 | 970.688 | 226.96 | 1203.57 | 89.5019 | 1711.01 | 80.2902
[18 empty] | 269.935 | 390.252 | [12 empty] | 970.688 | 336.114 | 1186.11 | 132.546 | 1663.46 | 119.527
[18 empty] | 269.935 | 600.082 | [12 empty] | 967.653 | 526.093 | 1172.56 | 206.6 | 1617.23 | 198.561
[32 empty] | 965.635 | 600.082 | 1166.46 | 358.598 | 1572.28 | 343.567
[34 empty] | 1167.68 | 538.321 | 1552.71 | 465.582
[34 empty] | 1168.9 | 601.337 | 1546.24 | 540.574
[36 empty] | 1547.86 | 602.594