## 123_6
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal, Extra Performance, Indicating, and Open Styles | [9 empty] | Universal, Extra Performance, Indicating, and Open Styles | [9 empty] | Universal, Extra Performance, Indicating, and Open Styles | [9 empty] | Universal, Extra Performance, Indicating, and Open Styles
Standard Speed (TCC 123-6) | [9 empty] | Standard Speed (TCC 123-6) | [9 empty] | Standard Speed (TCC 123-6) | [9 empty] | Standard Speed (TCC 123-6)
Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986
Tolerance in Terms of Current: Plus 10% for links rated 7 thru 100 std.; Plus 20% for links rated 125 thru 200 std. | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 7 thru 100 amps; Plus 20% for links rated 125 thru 200 amps | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 7 thru 100 amps; Plus 20% for links rated 125 thru 200 amps | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 7 thru 100 amps; Plus 20% for links rated 125 thru 200 amps
1 |  | 2 |  | 3 |  | 5 |  | 7 |  | 10 |  | 15 |  | 20 |  | 25 |  | 30 |  | 40 |  | 50 |  | 65 |  | 80 |  | 100 |  | 125 |  | 150 |  | 200
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
50.1664 | 0.01 | 93.0694 | 0.01 | 142.358 | 0.01 | 226.635 | 0.01 | 341.498 | 0.01 | 517.155 | 0.01 | 787.09 | 0.01 | 999.588 | 0.01 | 1177.72 | 0.01 | 1438.48 | 0.01 | 1941.74 | 0.01 | 2431.69 | 0.01 | 2964.13 | 0.01 | 3675.12 | 0.01 | 4848.09 | 0.01 | 6029.02 | 0.01 | 7858.41 | 0.01 | 9940.17 | 0.01
47.0564 | 0.011377 | 86.8642 | 0.011468 | 133.933 | 0.01132 | 207.129 | 0.012008 | 318.73 | 0.011503 | 467.006 | 0.012399 | 730.948 | 0.011618 | 932.009 | 0.011526 | 1086.09 | 0.011782 | 1273.26 | 0.012827 | 1734.27 | 0.012486 | 2280.93 | 0.011354 | 2802.7 | 0.011219 | 3440.39 | 0.011388 | 4565.76 | 0.011343 | 5615.8 | 0.01156 | 7512.62 | 0.010964 | 9598.29 | 0.01079
43.7874 | 0.013126 | 80.6683 | 0.013298 | 123.76 | 0.013298 | 190.251 | 0.014276 | 293.637 | 0.013621 | 424.683 | 0.014978 | 671.385 | 0.01384 | 858.634 | 0.01358 | 1002.59 | 0.013854 | 1156.71 | 0.015481 | 1558.28 | 0.01545 | 2086.7 | 0.013539 | 2600.19 | 0.013073 | 3185.42 | 0.013231 | 4223.17 | 0.013271 | 5091.56 | 0.01412 | 6990.73 | 0.012636 | 9048.37 | 0.012202
40.7863 | 0.015144 | 73.7991 | 0.015888 | 111.647 | 0.016438 | 172.491 | 0.017402 | 268.364 | 0.016307 | 386.968 | 0.018004 | 619.767 | 0.016226 | 772.277 | 0.01677 | 919.052 | 0.01652 | 1055.04 | 0.018682 | 1405.77 | 0.019022 | 1914.75 | 0.01608 | 2407.49 | 0.01522 | 2934.64 | 0.015636 | 3809.83 | 0.016389 | 4700.11 | 0.016603 | 6414.65 | 0.014933 | 8302.73 | 0.014448
37.915 | 0.017489 | 68.3982 | 0.018441 | 101.427 | 0.019877 | 156.232 | 0.021191 | 246.003 | 0.019484 | 352.251 | 0.021728 | 569.263 | 0.019136 | 704.398 | 0.020198 | 835.761 | 0.019957 | 951.788 | 0.022865 | 1265.65 | 0.02335 | 1779.95 | 0.018608 | 2224.62 | 0.017771 | 2700.9 | 0.018478 | 3468.02 | 0.019798 | 4282.71 | 0.019997 | 5868.42 | 0.017789 | 7819.22 | 0.016307
35.2458 | 0.020178 | 62.5112 | 0.0221 | 89.6888 | 0.025472 | 140.66 | 0.026195 | 225.731 | 0.023141 | 315.558 | 0.026859 | 516.122 | 0.023303 | 644.415 | 0.024061 | 753.963 | 0.024498 | 858.634 | 0.027955 | 1145.2 | 0.028462 | 1608.95 | 0.02275 | 2035.18 | 0.021212 | 2465.97 | 0.022144 | 3179.06 | 0.023467 | 3879.03 | 0.024425 | 5444.39 | 0.020689 | 7268.75 | 0.018889
32.8301 | 0.023303 | 56.6191 | 0.026725 | 80.0255 | 0.031931 | 128.939 | 0.03105 | 203.842 | 0.028406 | 285.815 | 0.032838 | 472.644 | 0.027732 | 585.428 | 0.029241 | 680.851 | 0.030192 | 776.148 | 0.034315 | 1020.8 | 0.035716 | 1485.25 | 0.026698 | 1845.19 | 0.025805 | 2269.56 | 0.026143 | 2856.47 | 0.029183 | 3516.92 | 0.029773 | 4916.44 | 0.025421 | 6709.91 | 0.0221
30.5494 | 0.026805 | 51.4879 | 0.032349 | 71.4749 | 0.040189 | 117.137 | 0.037547 | 180.61 | 0.036039 | 258.357 | 0.040149 | 419.617 | 0.035149 | 533.438 | 0.035254 | 618.528 | 0.036583 | 690.45 | 0.043232 | 891.89 | 0.046646 | 1321.26 | 0.033602 | 1643.1 | 0.032446 | 2065.94 | 0.031519 | 2589.81 | 0.035431 | 3163.2 | 0.036767 | 4493.29 | 0.030374 | 6071.37 | 0.026859
28.3988 | 0.03105 | 46.2169 | 0.040028 | 62.7618 | 0.052174 | 106.521 | 0.045677 | 162.934 | 0.044549 | 235.649 | 0.048115 | 372.54 | 0.044549 | 487.038 | 0.042123 | 570.403 | 0.04306 | 625.37 | 0.052804 | 811.061 | 0.05652 | 1196.72 | 0.041042 | 1467.53 | 0.040593 | 1891.91 | 0.03766 | 2338.68 | 0.043362 | 2893.84 | 0.044106 | 4156.13 | 0.035466 | 5587.8 | 0.031614
26.5053 | 0.035751 | 41.6519 | 0.049136 | 55.5535 | 0.066526 | 96.2882 | 0.055678 | 147.281 | 0.054576 | 212.585 | 0.05924 | 331.074 | 0.05652 | 445.565 | 0.050632 | 530.247 | 0.049878 | 558.549 | 0.065864 | 721.508 | 0.071349 | 1080.67 | 0.050229 | 1329.21 | 0.049333 | 1718.73 | 0.045814 | 2139.53 | 0.051862 | 2626.32 | 0.053549 | 3806.02 | 0.042376 | 4990.74 | 0.039551
24.5656 | 0.041454 | 37.9529 | 0.05924 | 50.62 | 0.080286 | 85.0591 | 0.071421 | 133.799 | 0.066128 | 191.396 | 0.072791 | 298.97 | 0.069657 | 411.308 | 0.059656 | 484.125 | 0.059955 | 494.894 | 0.083562 | 644.415 | 0.089442 | 967.14 | 0.062464 | 1195.52 | 0.06135 | 1559.84 | 0.055401 | 1957.34 | 0.062028 | 2352.75 | 0.066659 | 3481.92 | 0.050835 | 4565.76 | 0.047209
22.9277 | 0.047684 | 34.1699 | 0.072791 | 46.0785 | 0.096505 | 76.5042 | 0.08811 | 123.142 | 0.078382 | 172.491 | 0.0898 | 269.979 | 0.085421 | 368.833 | 0.073817 | 437.179 | 0.073449 | 450.944 | 0.10064 | 570.403 | 0.11348 | 856.062 | 0.079726 | 1072.06 | 0.076217 | 1411.4 | 0.068006 | 1796.04 | 0.07367 | 2145.96 | 0.080607 | 3141.14 | 0.062652 | 4118.9 | 0.058125
21.2923 | 0.055179 | 30.4884 | 0.091523 | 42.9633 | 0.1109 | 68.2615 | 0.11078 | 112.431 | 0.09384 | 157.487 | 0.1073 | 243.312 | 0.10507 | 322.9 | 0.095927 | 386.582 | 0.094122 | 412.957 | 0.12037 | 498.869 | 0.14865 | 766.89 | 0.098948 | 951.788 | 0.096505 | 1286.06 | 0.082154 | 1634.9 | 0.089263 | 1980.97 | 0.094783 | 2816.75 | 0.078069 | 3760.62 | 0.070147
19.833 | 0.063662 | 27.6423 | 0.11145 | 39.7793 | 0.12949 | 61.8892 | 0.13464 | 101.529 | 0.11508 | 143.501 | 0.12923 | 220.157 | 0.12833 | 294.519 | 0.11508 | 344.586 | 0.11858 | 371.424 | 0.1482 | 452.299 | 0.18102 | 685.633 | 0.12429 | 855.206 | 0.11953 | 1170.68 | 0.098849 | 1488.22 | 0.10794 | 1815.91 | 0.11224 | 2551.25 | 0.095258 | 3399.35 | 0.086452
18.4367 | 0.073596 | 24.3698 | 0.14382 | 36.9788 | 0.14984 | 55.6091 | 0.1676 | 90.9533 | 0.14397 | 130.626 | 0.15643 | 197.422 | 0.16007 | 269.17 | 0.13832 | 317.14 | 0.13999 | 329.423 | 0.18822 | 405.59 | 0.22579 | 617.91 | 0.15318 | 781.6 | 0.14311 | 1038.3 | 0.12504 | 1333.2 | 0.1341 | 1644.74 | 0.13681 | 2308.47 | 0.11588 | 3094.37 | 0.10538
17.1903 | 0.08474 | 21.6357 | 0.18265 | 33.393 | 0.1843 | 50.4179 | 0.20369 | 82.876 | 0.1734 | 117.842 | 0.19106 | 178.456 | 0.1957 | 248.973 | 0.16184 | 288.398 | 0.16929 | 289.554 | 0.24289 | 374.407 | 0.26417 | 556.32 | 0.18897 | 711.477 | 0.17271 | 932.942 | 0.15487 | 1218.45 | 0.16087 | 1509.21 | 0.16281 | 2097.16 | 0.14154 | 2836.54 | 0.12743
15.9641 | 0.098061 | 19.324 | 0.22715 | 30.3667 | 0.22265 | 45.2113 | 0.2533 | 75.3652 | 0.20989 | 106.308 | 0.23383 | 161.635 | 0.23831 | 232.373 | 0.18672 | 264.633 | 0.20166 | 270.249 | 0.27855 | 347.006 | 0.30692 | 497.374 | 0.23665 | 652.195 | 0.20553 | 842.474 | 0.19011 | 1101.4 | 0.19668 | 1386.22 | 0.19414 | 1912.83 | 0.17167 | 2628.95 | 0.15014
14.8254 | 0.11359 | 17.4676 | 0.27688 | 27.8643 | 0.26443 | 40.8271 | 0.31156 | 69.5013 | 0.2473 | 97.1587 | 0.28135 | 144.798 | 0.29905 | 217.097 | 0.2137 | 240.169 | 0.24557 | 247.731 | 0.33448 | 322.9 | 0.35552 | 446.904 | 0.29548 | 592.495 | 0.24804 | 760.019 | 0.23243 | 1012.66 | 0.2343 | 1277.09 | 0.23035 | 1749.95 | 0.2078 | 2478.33 | 0.1715
13.713 | 0.1325 | 16.3356 | 0.31501 | 25.2631 | 0.32298 | 36.9419 | 0.37978 | 62.7618 | 0.3057 | 89.0632 | 0.33583 | 131.544 | 0.36307 | 203.231 | 0.2441 | 218.185 | 0.29755 | 228.684 | 0.39567 | 301.673 | 0.40936 | 405.996 | 0.36018 | 548.037 | 0.29224 | 683.58 | 0.29021 | 930.147 | 0.27771 | 1163.68 | 0.27994 | 1599.33 | 0.25407 | 2306.16 | 0.20045
12.7859 | 0.15196 | 15.2008 | 0.36307 | 22.8819 | 0.39449 | 34.5479 | 0.43729 | 56.2804 | 0.38398 | 79.6264 | 0.42436 | 117.02 | 0.46294 | 189.871 | 0.28023 | 197.027 | 0.36562 | 207.959 | 0.48087 | 280.155 | 0.47847 | 372.912 | 0.42906 | 506.915 | 0.34433 | 613.6 | 0.36162 | 860.353 | 0.32363 | 1083.92 | 0.32753 | 1469 | 0.30631 | 2114.01 | 0.24386
11.8384 | 0.1769 | 14.0883 | 0.42267 | 20.829 | 0.47371 | 32.4385 | 0.49949 | 51.3336 | 0.46806 | 71.4034 | 0.53517 | 105.145 | 0.57917 | 175.975 | 0.32688 | 182.061 | 0.4282 | 191.013 | 0.57686 | 262.262 | 0.55258 | 349.794 | 0.49009 | 473.591 | 0.39607 | 560.228 | 0.43773 | 792.619 | 0.38207 | 1011.65 | 0.38054 | 1366.95 | 0.36018 | 1943.68 | 0.29607
10.9501 | 0.20697 | 13.0442 | 0.49403 | 18.7528 | 0.58792 | 30.2455 | 0.58265 | 47.8153 | 0.5449 | 64.3506 | 0.66954 | 95.521 | 0.71308 | 164.407 | 0.37675 | 166.724 | 0.51522 | 172.146 | 0.71953 | 244.776 | 0.64072 | 328.436 | 0.55925 | 440.691 | 0.46063 | 515.091 | 0.52353 | 741.995 | 0.43729 | 966.173 | 0.42436 | 1268.18 | 0.42906 | 1783.51 | 0.3609
10.2098 | 0.23831 | 12.2478 | 0.56318 | 17.1046 | 0.7074 | 28.2007 | 0.67695 | 44.672 | 0.63181 | 58.4602 | 0.82517 | 89.6888 | 0.81615 | 152.375 | 0.43685 | 153.752 | 0.60825 | 156.076 | 0.89033 | 228.227 | 0.74665 | 309.619 | 0.63435 | 410.076 | 0.53625 | 476.441 | 0.61745 | 689.76 | 0.51009 | 914.468 | 0.48231 | 1173.02 | 0.51574 | 1667.93 | 0.42352
9.406 | 0.28107 | 11.3742 | 0.65826 | 15.7895 | 0.82848 | 26.4524 | 0.78024 | 41.9025 | 0.72676 | 52.8441 | 1.0334 | 83.5417 | 0.95108 | 140.519 | 0.51368 | 143.932 | 0.69966 | 142.928 | 1.0831 | 211.525 | 0.88678 | 292.757 | 0.71666 | 383.885 | 0.6193 | 440.25 | 0.73627 | 639.92 | 0.60341 | 866.397 | 0.54982 | 1088.26 | 0.61621 | 1532.02 | 0.52196
8.6915 | 0.32885 | 10.6904 | 0.7474 | 14.7515 | 0.95489 | 24.8125 | 0.90108 | 39.2655 | 0.83932 | 48.8301 | 1.2446 | 78.598 | 1.0907 | 129.715 | 0.60643 | 134.874 | 0.804 | 132.336 | 1.2941 | 195.067 | 1.0659 | 277.923 | 0.80803 | 361.168 | 0.71023 | 413.784 | 0.84353 | 594.276 | 0.70457 | 814.311 | 0.6388 | 1020.8 | 0.72169 | 1405.77 | 0.64393
7.9038 | 0.39213 | 10.0276 | 0.85799 | 13.7267 | 1.105 | 23.2975 | 1.0375 | 36.8681 | 0.96835 | 45.5744 | 1.4664 | 74.0948 | 1.2421 | 121.674 | 0.69408 | 127.401 | 0.91105 | 125.63 | 1.4679 | 181.516 | 1.2596 | 263.313 | 0.91653 | 335.071 | 0.83514 | 389.297 | 0.96835 | 558.549 | 0.80722 | 774.597 | 0.72531 | 966.173 | 0.83264 | 1319.94 | 0.75869
7.2525 | 0.46294 | 9.4437 | 0.97418 | 12.9144 | 1.2609 | 22.117 | 1.1675 | 34.6863 | 1.1161 | 43.3084 | 1.6634 | 69.7799 | 1.4231 | 112.995 | 0.81208 | 120.704 | 1.0282 | 119.742 | 1.6501 | 172.318 | 1.4374 | 250.972 | 1.0211 | 316.19 | 0.9568 | 368.464 | 1.1017 | 523.399 | 0.93692 | 724.399 | 0.86229 | 919.972 | 0.94633 | 1256.82 | 0.86143
6.6615 | 0.54708 | 8.876 | 1.1116 | 12.1017 | 1.4577 | 20.829 | 1.3349 | 32.6011 | 1.2902 | 41.1962 | 1.8924 | 65.6505 | 1.6419 | 103.891 | 0.97515 | 115.971 | 1.1206 | 114.359 | 1.8494 | 163.26 | 1.6501 | 238.494 | 1.1535 | 300.469 | 1.0842 | 349.095 | 1.2484 | 487.038 | 1.1039 | 684.263 | 1.0018 | 873.356 | 1.0885 | 1200.31 | 0.97418
6.1617 | 0.63816 | 8.2594 | 1.2928 | 11.4198 | 1.6717 | 19.8131 | 1.5051 | 30.7333 | 1.4886 | 39.3441 | 2.1273 | 62.8874 | 1.8164 | 96.0958 | 1.1582 | 110.647 | 1.2509 | 109.327 | 2.0685 | 155.92 | 1.8568 | 225.28 | 1.3296 | 283.821 | 1.2496 | 330.083 | 1.4317 | 453.204 | 1.3163 | 656.776 | 1.1172 | 830.762 | 1.2609 | 1145.2 | 1.1105
5.7509 | 0.73333 | 7.8096 | 1.4591 | 10.8411 | 1.8886 | 18.7716 | 1.7174 | 29.3222 | 1.6717 | 37.8771 | 2.3463 | 60.482 | 1.9894 | 91.1353 | 1.3045 | 104.099 | 1.4432 | 103.787 | 2.3889 | 149.806 | 2.0768 | 214.079 | 1.5141 | 271.603 | 1.3991 | 314.928 | 1.6126 | 429.38 | 1.5036 | 626.622 | 1.2761 | 795.796 | 1.4317 | 1102.5 | 1.2434
5.3567 | 0.8503 | 7.4734 | 1.611 | 10.3537 | 2.123 | 17.9098 | 1.9384 | 28.2289 | 1.8457 | 36.138 | 2.6561 | 57.4748 | 2.2633 | 85.1442 | 1.5309 | 98.8245 | 1.6419 | 99.5187 | 2.672 | 143.501 | 2.323 | 204.659 | 1.7072 | 258.357 | 1.5981 | 301.371 | 1.8091 | 406.809 | 1.7192 | 595.465 | 1.4782 | 765.357 | 1.611 | 1067.78 | 1.3632
5.0146 | 0.97808 | 7.1804 | 1.7697 | 9.9677 | 2.3463 | 17.0193 | 2.2008 | 27.0408 | 2.0623 | 34.617 | 2.9827 | 54.8908 | 2.5545 | 80.0255 | 1.7733 | 94.476 | 1.8401 | 95.6165 | 2.9977 | 137.187 | 2.6454 | 194.288 | 1.9815 | 244.043 | 1.8679 | 287.822 | 2.0418 | 388.131 | 1.9539 | 566.424 | 1.7106 | 726.576 | 1.8962 | 1040.38 | 1.4827
4.732 | 1.1161 | 6.8713 | 1.9696 | 9.6731 | 2.5596 | 16.3029 | 2.4617 | 25.9805 | 2.2792 | 33.4264 | 3.2866 | 52.266 | 2.9091 | 76.0466 | 2.0114 | 90.1384 | 2.081 | 91.7755 | 3.3968 | 131.281 | 3.0218 | 185.925 | 2.2543 | 231.677 | 2.1637 | 276.26 | 2.2838 | 371.052 | 2.2097 | 542.042 | 1.9657 | 700.884 | 2.1422 | 1005.6 | 1.6534
4.4564 | 1.2864 | 6.5624 | 2.2386 | 9.3685 | 2.8259 | 15.648 | 2.726 | 24.8125 | 2.5673 | 32.471 | 3.571 | 50.2166 | 3.2376 | 71.8331 | 2.3346 | 86.2583 | 2.3346 | 87.9128 | 3.8956 | 127.274 | 3.3429 | 178.278 | 2.557 | 220.819 | 2.4939 | 262 | 2.6507 | 356.86 | 2.4814 | 521.309 | 2.2296 | 674.076 | 2.4592 | 976.859 | 1.8291
4.2095 | 1.4723 | 6.3684 | 2.4592 | 9.0916 | 3.1231 | 15.1704 | 2.959 | 23.7206 | 2.8888 | 31.4169 | 3.9505 | 48.1031 | 3.6541 | 67.8532 | 2.7124 | 82.876 | 2.6191 | 84.2127 | 4.4944 | 123.76 | 3.6687 | 171.459 | 2.8543 | 210.47 | 2.8975 | 250.722 | 3.0308 | 342.867 | 2.7866 | 500.368 | 2.5647 | 648.942 | 2.8231 | 942.318 | 2.0562
3.9604 | 1.7072 | 6.1248 | 2.8006 | 8.8671 | 3.4207 | 14.7958 | 3.1514 | 22.6996 | 3.2539 | 30.2757 | 4.4099 | 46.4022 | 4.0586 | 64.8674 | 3.0766 | 79.5468 | 2.9442 | 81.3162 | 5.0827 | 120.342 | 4.0465 | 165.231 | 3.2247 | 202.42 | 3.2964 | 240.409 | 3.4655 | 329.753 | 3.1357 | 485.094 | 2.8515 | 627.876 | 3.215 | 913.554 | 2.2998
3.7447 | 1.9676 | 5.8847 | 3.2997 | 8.6051 | 3.8376 | 14.3442 | 3.4551 | 21.8532 | 3.5997 | 29.2636 | 4.9128 | 44.6273 | 4.5898 | 61.9511 | 3.5038 | 76.1988 | 3.3529 | 79.3085 | 5.6173 | 116.903 | 4.5487 | 159.707 | 3.6286 | 195.067 | 3.7578 | 232.605 | 3.8607 | 320.327 | 3.4551 | 468.41 | 3.2604 | 609.32 | 3.6541 | 884.783 | 2.5801
3.5443 | 2.2724 | 5.7222 | 3.7428 | 8.3674 | 4.2795 | 13.9063 | 3.8223 | 20.9963 | 4.0303 | 28.1443 | 5.5781 | 43.1786 | 5.0929 | 59.2251 | 3.9982 | 73.6516 | 3.7316 | 77.8159 | 6.0851 | 113.789 | 5.1441 | 154.987 | 4.0465 | 189.113 | 4.2158 | 226.183 | 4.2838 | 310.86 | 3.8684 | 452.751 | 3.6871 | 594.276 | 4.1076 | 854.352 | 2.9679
3.3748 | 2.6218 | 5.5642 | 4.3312 | 8.1364 | 4.859 | 13.5494 | 4.1864 | 20.2336 | 4.5125 | 27.2035 | 6.2956 | 41.9444 | 5.5669 | 56.6757 | 4.5761 | 71.3321 | 4.1739 | 75.8946 | 6.8472 | 110.757 | 5.8524 | 151.463 | 4.4542 | 183.891 | 4.7249 | 220.157 | 4.7533 | 301.975 | 4.3879 | 437.617 | 4.1906 | 581.344 | 4.6313 | 827.445 | 3.39
3.2231 | 3.0067 | 5.4214 | 4.9523 | 7.9038 | 5.668 | 13.2281 | 4.6036 | 19.382 | 5.1492 | 26.2154 | 7.1911 | 40.8271 | 6.1278 | 54.4534 | 5.2375 | 69.0165 | 4.7296 | 74.2432 | 7.7202 | 108.239 | 6.5919 | 148.019 | 4.9079 | 178.813 | 5.3647 | 213.865 | 5.4132 | 293.93 | 4.997 | 422.988 | 4.8059 | 569.263 | 5.1647 | 799.785 | 3.9112
3.1185 | 3.3664 | 5.277 | 5.7825 | 7.6856 | 6.6449 | 12.85 | 5.201 | 18.4921 | 5.9646 | 25.3644 | 8.0917 | 39.6998 | 6.8063 | 52.528 | 5.923 | 66.5761 | 5.4622 | 72.7731 | 8.8096 | 105.25 | 7.7279 | 145.233 | 5.3433 | 174.573 | 6.0548 | 209.211 | 6.0608 | 286.673 | 5.6567 | 409.666 | 5.5447 | 555.208 | 5.9053 | 776.148 | 4.4944
3.0354 | 3.7056 | 5.1467 | 6.7385 | 7.5033 | 7.79 | 12.5202 | 5.8524 | 17.7848 | 6.8131 | 24.6887 | 8.9696 | 38.6809 | 7.5296 | 50.7213 | 6.7723 | 64.415 | 6.2641 | 71.4749 | 10.0627 | 102.754 | 8.9249 | 142.215 | 5.9349 | 170.093 | 6.9368 | 203.638 | 6.9299 | 280.435 | 6.3843 | 395.972 | 6.442 | 544.759 | 6.6051 | 756.985 | 5.0422
2.9575 | 4.1365 | 5.0347 | 7.7357 | 7.3327 | 9.0961 | 12.2233 | 6.6648 | 17.2247 | 7.5977 | 24.1032 | 9.9428 | 37.7259 | 8.3632 | 49.3702 | 7.4846 | 61.9511 | 7.4249 | 70.2701 | 11.5749 | 100.217 | 10.6317 | 138.982 | 6.6449 | 166.059 | 7.9236 | 199.406 | 7.8841 | 273.785 | 7.2706 | 383.501 | 7.4846 | 529.717 | 7.7125 | 740.513 | 5.6173
2.8874 | 4.6452 | 4.935 | 8.9966 | 7.1875 | 10.6211 | 11.9813 | 7.3879 | 16.8499 | 8.2717 | 23.5787 | 11.1322 | 36.7209 | 9.4768 | 48.2959 | 8.2058 | 60.2406 | 8.3968 | 68.9475 | 13.7473 | 97.8412 | 12.6018 | 135.957 | 7.4622 | 161.474 | 9.3637 | 194.483 | 9.1875 | 267.56 | 8.3382 | 374.033 | 8.5493 | 518.709 | 8.8008 | 728.759 | 6.1647
2.8133 | 5.2585 | 4.8373 | 10.3588 | 7.0311 | 12.665 | 11.7206 | 8.3884 | 16.4833 | 9.1052 | 23.0888 | 12.5892 | 35.9578 | 10.6957 | 47.3869 | 8.9786 | 58.7532 | 9.572 | 68.057 | 15.75 | 95.9998 | 14.9669 | 132.999 | 8.4136 | 157.802 | 10.9336 | 190.251 | 10.5575 | 261.738 | 9.62 | 366.626 | 9.4768 | 508.947 | 10.0829 | 718.627 | 6.8267
2.7576 | 5.8641 | 4.751 | 12.0353 | 6.8302 | 16.1649 | 11.4885 | 9.6296 | 16.1569 | 9.9826 | 22.5864 | 14.6266 | 35.1402 | 12.1684 | 46.6348 | 9.7264 | 57.5898 | 10.7493 | 67.1109 | 18.4275 | 94.193 | 17.7581 | 129.456 | 9.9229 | 154.523 | 12.539 | 187.231 | 11.9872 | 255.786 | 11.5057 | 360.446 | 10.6105 | 500.868 | 11.4483 | 701.586 | 7.9633
2.6895 | 6.7453 | 4.6616 | 14.337 | 6.6749 | 19.7834 | 11.261 | 11.0435 | 15.9004 | 10.9665 | 22.1613 | 16.6406 | 34.3756 | 13.8162 | 45.9405 | 10.7493 | 56.5625 | 12.1684 | 66.5096 | 20.6733 | 92.8835 | 20.5291 | 126.893 | 11.2553 | 151.918 | 14.4088 | 182.974 | 14.1943 | 250.722 | 13.4213 | 356.503 | 11.8442 | 494.399 | 12.9338 | 690.45 | 9.0146
2.6178 | 7.8605 | 4.5784 | 16.9428 | 6.5558 | 23.9231 | 11.049 | 12.7667 | 15.57 | 12.5264 | 21.7442 | 19.6847 | 33.6949 | 15.6715 | 45.2113 | 12.0714 | 55.7204 | 13.7198 | 65.8478 | 22.9162 | 91.7755 | 23.5669 | 124.256 | 12.9986 | 149.208 | 16.5576 | 178.992 | 17.0448 | 246.249 | 15.6558 | 352.603 | 13.6105 | 488.502 | 14.5246 | 679.49 | 10.4212
2.5583 | 8.9966 | 4.4877 | 20.7562 | 6.4453 | 28.987 | 10.8628 | 14.7294 | 15.3229 | 14.166 | 21.399 | 23.0541 | 33.0938 | 18.0626 | 44.4047 | 13.8439 | 54.8908 | 15.7816 | 65.2578 | 25.7348 | 90.6808 | 27.6837 | 121.917 | 14.9669 | 146.84 | 18.9318 | 176.151 | 19.8032 | 241.856 | 18.5199 | 350.494 | 15.8765 | 481.229 | 16.9598 | 669.374 | 12.0353
2.5127 | 10.1842 | 4.4033 | 25.1245 | 6.3557 | 33.0442 | 10.7118 | 17.0789 | 15.0947 | 16.0682 | 21.0804 | 27.4632 | 32.5034 | 21.1543 | 43.3951 | 16.6073 | 54.2361 | 17.9366 | 64.6085 | 30.4427 | 89.5991 | 32.2283 | 120.222 | 17.0448 | 144.798 | 21.8859 | 173.529 | 23.3091 | 237.779 | 22.128 | 347.354 | 18.5941 | 475.489 | 19.7044 | 662.051 | 13.4751
2.4678 | 11.5634 | 4.3247 | 30.0796 | 6.2799 | 38.1241 | 10.5734 | 19.6062 | 14.8551 | 18.4829 | 20.829 | 32.7481 | 31.9875 | 24.627 | 42.7063 | 19.3917 | 53.5891 | 20.7354 | 64.0296 | 36.6292 | 88.5304 | 37.6317 | 118.196 | 19.5279 | 142.073 | 27.1627 | 171.116 | 28.2148 | 234.943 | 25.5809 | 345.276 | 21.9737 | 469.817 | 23.0541 | 654.809 | 15.2388
2.4141 | 13.6105 | 4.2646 | 35.1578 | 6.2174 | 43.7218 | 10.4369 | 22.6202 | 14.634 | 21.0278 | 20.6011 | 39.0502 | 31.5744 | 28.4414 | 42.1547 | 22.2389 | 53.0559 | 24.309 | 63.5194 | 44.0289 | 87.2123 | 44.5605 | 116.32 | 22.7791 | 139.958 | 33.3763 | 169.244 | 32.5848 | 231.445 | 30.3819 | 342.524 | 25.9415 | 463.749 | 27.2443 | 646.998 | 17.6872
2.383 | 15.6715 | 4.2137 | 40.9703 | 6.174 | 49.9413 | 10.3227 | 26.0716 | 14.4594 | 24.5778 | 20.437 | 47.696 | 31.229 | 33.2763 | 41.6935 | 25.7863 | 52.423 | 29.4545 | 62.8874 | 53.2953 | 86.2583 | 52.24 | 115.047 | 26.1761 | 138.427 | 41.2994 | 167.393 | 38.9721 | 229.142 | 34.8777 | 339.456 | 29.5725 | 460.514 | 30.5342 | 643.128 | 20.3045
2.3451 | 18.4644 | 4.1676 | 48.6109 | 6.1187 | 57.8497 | 10.1996 | 30.1097 | 14.3012 | 28.5268 | 20.3147 | 59.9103 | 30.8565 | 39.5611 | 41.2374 | 30.2606 | 51.9533 | 35.1578 | 62.4487 | 66.3437 | 85.4854 | 60.7549 | 113.561 | 29.9595 | 137.187 | 49.6425 | 165.727 | 47.4107 | 226.862 | 40.32 | 335.071 | 34.187 | 454.112 | 35.0174 | 638.003 | 23.1234
2.3125 | 21.3029 | 4.1179 | 59.2549 | 6.076 | 67.2118 | 10.1183 | 34.8428 | 14.1731 | 33.6444 | 20.2539 | 72.0852 | 30.6106 | 46.379 | 40.8679 | 36.7393 | 51.5909 | 42.6423 | 61.8892 | 81.5201 | 84.6348 | 71.1542 | 112.207 | 34.5997 | 135.686 | 62.6052 | 164.571 | 56.7042 | 223.261 | 48.3201 | 331.074 | 38.086 | 448.246 | 40.159 | 631.023 | 26.1499
2.2872 | 24.4553 | 4.0851 | 70.6578 | 6.0457 | 78.8738 | 10.0779 | 40.1992 | 14.0742 | 39.0892 | 20.2336 | 90.0036 | 30.4275 | 54.6445 | 40.5423 | 44.6051 | 51.2823 | 51.5137 | 61.5805 | 103.012 | 83.9604 | 84.2551 | 110.868 | 39.9188 | 134.47 | 80.3867 | 163.26 | 68.9822 | 219.279 | 60.3311 | 327.453 | 42.4296 | 444.23 | 44.9184 | 621.629 | 30.3212
2.2532 | 29.1322 | 4.0526 | 84.7622 | 6.0095 | 93.2095 | 10.0578 | 46.5649 | 14.004 | 46.5184 | 20.173 | 111.146 | 30.2757 | 66.4765 | 40.3805 | 53.242 | 51.0776 | 64.3186 | 61.2734 | 126.45 | 83.125 | 101.58 | 109.546 | 46.4719 | 133.666 | 100.168 | 161.797 | 85.1019 | 216.446 | 70.5872 | 324.194 | 46.3327 | 439.371 | 49.7419 | 609.929 | 35.9758
2.2308 | 34.2555 | 4.0203 | 101.58 | 5.9796 | 112.488 | 10.0176 | 54.2633 | 13.9481 | 55.9159 | 20.1327 | 139.889 | 30.1549 | 80.0658 | 40.3401 | 64.8352 | 50.9246 | 80.5477 | 61.0288 | 159.15 | 82.6278 | 120.283 | 108.347 | 53.402 | 132.468 | 124.07 | 160.829 | 106.043 | 213.865 | 82.0927 | 319.368 | 52.765 | 433.696 | 56.2524 | 596.061 | 43.4603
2.2064 | 39.7594 | 4.0082 | 124.443 | 5.9676 | 131.874 | 9.9876 | 64.3829 | 13.9063 | 67.2118 | 20.0724 | 172.751 | 30.1247 | 96.1442 | 40.2595 | 79.826 | 50.8737 | 102.396 | 60.7244 | 194.387 | 82.2157 | 145.743 | 107.162 | 62.1064 | 131.15 | 155.999 | 160.027 | 130.171 | 211.948 | 94.8076 | 314.298 | 59.3142 | 426.812 | 64.5764 | 586.014 | 49.8914
2.1888 | 46.5649 | 4.0042 | 147.65 | 5.9676 | 157.409 | 9.9777 | 77.933 | 13.8924 | 80.0658 | 20.0123 | 214.401 | 30.0946 | 115.336 | 40.0988 | 96.8196 | 50.7213 | 126.197 | 60.4216 | 224.719 | 81.8056 | 168.149 | 106.096 | 72.2295 | 130.365 | 193.998 | 159.388 | 164.325 | 209.63 | 110.15 | 308.075 | 67.5487 | 419.617 | 72.9554 | 573.262 | 58.0816
2.1735 | 53.1888 | 3.9922 | 172.405 | 5.9676 | 194.776 | 9.9777 | 92.8374 | 13.9063 | 95.7604 | 19.9523 | 243.922 | 30.0045 | 142.857 | 40.0988 | 123.822 | 50.62 | 158.356 | 60.2406 | 259.524 | 81.3162 | 191.301 | 105.145 | 84.6774 | 129.586 | 234.124 | 159.388 | 202.522 | 207.129 | 135.348 | 303.185 | 74.9521 | 411.72 | 83.0838 | 560.788 | 67.4137
2.1584 | 61.3655 | 3.9882 | 205.172 | 5.9617 | 238.376 | 9.9577 | 111.146 | 13.8924 | 120.644 | 19.9523 | 275.572 | 30.0045 | 173.964 | 40.0587 | 151.237 | 50.4683 | 195.752 | 59.9401 | 303.946 | 80.749 | 224.719 | 104.307 | 99.2706 | 129.197 | 265.297 | 159.388 | 226.75 | 205.068 | 159.788 | 295.404 | 87.7814 | 403.164 | 94.1463 | 546.396 | 78.6375
2.1347 | 75.4031 | 3.9842 | 249.348 | 5.9617 | 268.232 | 9.9577 | 139.33 | 13.8924 | 148.242 | 19.9523 | 301.524 | 29.9745 | 218.733 | 39.7793 | 183.25 | 50.3172 | 242.949 |  |  | 80.1858 | 263.71 | 103.476 | 120.886 | 128.939 | 297.928 | 159.229 | 259.524 | 203.638 | 185.276 | 289.554 | 100.168 | 393.997 | 107.323 | 530.778 | 92.3744
2.1156 | 88.1332 | 3.9803 | 298.226 | 5.9557 | 297.928 | 9.9577 | 172.233 | 13.8924 | 190.157 |  |  | 29.9745 | 259.524 | 39.6601 | 221.152 | 50.2166 | 268.232 |  |  | 79.6264 | 307.001 | 102.447 | 143.143 |  |  | 159.07 | 298.823 | 202.217 | 216.123 | 283.821 | 114.646 | 383.501 | 124.194 | 516.638 | 106.043
2.1051 | 102.498 |  |  |  |  | 9.9777 | 211.844 | 13.9063 | 226.977 |  |  | 29.9745 | 298.524 | 39.6601 | 259.524 | 50.1163 | 302.43 |  |  |  |  | 101.529 | 170.008 |  |  |  |  | 201.41 | 246.62 | 278.758 | 130.692 | 373.659 | 141.295 | 503.883 | 120.644
2.082 | 122.223 |  |  |  |  | 9.9577 | 249.598 | 13.8924 | 259.784 |  |  |  |  | 39.6205 | 300.021 | [6 empty] | 100.82 | 208.899 |  |  |  |  | 200.405 | 276.954 | 272.147 | 153.063 | 363.342 | 161.717 | 488.502 | 138.774
2.0654 | 142.715 |  |  |  |  | 9.9677 | 299.721 | 13.8924 | 300.321 | [12 empty] | 100.418 | 237.662 |  |  |  |  | 199.805 | 300.621 | 265.693 | 181.064 | 354.016 | 184.352 | 475.013 | 157.252
2.049 | 168.991 | [20 empty] | 100.017 | 269.307 | [6 empty] | 260.432 | 204.558 | 344.241 | 208.899 | 459.134 | 179.621
2.0347 | 194.387 | [20 empty] | 99.7179 | 306.081 | [6 empty] | 254.511 | 233.89 | 334.736 | 233.189 | 442.457 | 207.027
2.0185 | 226.524 | [28 empty] | 248.724 | 266.894 | 327.78 | 256.172 | 426.812 | 236.24
2.0044 | 259.524 | [28 empty] | 243.312 | 307.308 | 321.933 | 281.984 | 412.544 | 266.627
1.9924 | 301.223 | [28 empty] | 240.409 | 340.989 | 317.775 | 305.775 | 400.352 | 300.021
[30 empty] | 236.593 | 383.313 | 314.613 | 330.912 | 389.297 | 338.95
[30 empty] | 234.239 | 424.05 | 311.482 | 362.437 | 382.353 | 374.597
[30 empty] | 231.677 | 476.683 | 309.619 | 393.803 | 376.66 | 411.106
[30 empty] | 230.061 | 534.779 | 307.767 | 424.899 | 372.54 | 447.579
[30 empty] | 229.142 | 581.641 | 306.232 | 470.997 | 369.941 | 489.729
[30 empty] | 228.684 | 601.155 | 305.926 | 526.817 | 368.464 | 538.535
[32 empty] | 305.926 | 573.555 | 366.26 | 602.961
[32 empty] | 305.926 | 602.359