## 166_6
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles
"QR" Speed (TCC 166-6) | [9 empty] | Coordinating Speed (TCC 166-6) | [9 empty] | Coordinating Speed (TCC 166-6) | [9 empty] | Coordinating Speed (TCC 166-6)
Minimum Melting Time-Current Characteristic Curves Dated February 23, 1987 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated February 23, 1987 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated February 23, 1987 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated February 23, 1987
Tolerance in Terms of Current: Plus 10% for links rated 10QR thru 200QR | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 10QR thru 200QR | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 10QR thru 200QR | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 10QR thru 200QR
1QR |  | 2QR |  | 3QR |  | 5QR |  | 7QR |  | 10QR |  | 15QR |  | 20QR |  | 25QR |  | 30QR |  | 40QR |  | 50QR |  | 60QR |  | 75QR |  | 100QR |  | 125QR |  | 150QR SP |  | 150QR |  | 175QR |  | 200QR
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
50.1664 | 0.01 | 93.0694 | 0.01 | 142.358 | 0.01 | 157.96 | 0.01 | 226.635 | 0.01 | 384.654 | 0.01 | 491.442 | 0.01 | 705.808 | 0.01 | 869 | 0.01 | 1067.78 | 0.01 | 1352 | 0.01 | 1684.69 | 0.01 | 2103.46 | 0.01 | 2964.13 | 0.01 | 3809.83 | 0.01 | 5220.46 | 0.01 | 6150.82 | 0.01 | 6531.16 | 0.01 | 8097.74 | 0.01 | 9445.94 | 0.01
47.0564 | 0.011377 | 86.8642 | 0.011468 | 133.933 | 0.01132 | 151.918 | 0.010811 | 207.129 | 0.012008 | 361.168 | 0.011411 | 460.514 | 0.011457 | 660.729 | 0.01148 | 815.126 | 0.011411 | 1001.58 | 0.011434 | 1270.72 | 0.011366 | 1578.67 | 0.011411 | 1977.01 | 0.011354 | 2780.37 | 0.011457 | 3573.64 | 0.011411 | 4941.09 | 0.01123 | 5792.62 | 0.011286 | 6293.92 | 0.010811 | 7610.93 | 0.011309 | 9012.25 | 0.010887
43.7874 | 0.013126 | 80.6683 | 0.013298 | 123.76 | 0.013298 | 140.238 | 0.0127 | 190.251 | 0.014276 | 322.9 | 0.01429 | 414.612 | 0.014233 | 588.951 | 0.014477 | 723.675 | 0.01455 | 888.33 | 0.014564 | 1145.2 | 0.013993 | 1417.06 | 0.014106 | 1794.25 | 0.013771 | 2535.99 | 0.013758 | 3249.77 | 0.013758 | 4453.03 | 0.013771 | 5320.59 | 0.013404 | 5886.05 | 0.012411 | 6804.5 | 0.014134 | 8377.79 | 0.0127
40.7863 | 0.015144 | 73.7991 | 0.015888 | 111.647 | 0.016438 | 129.068 | 0.014993 | 172.491 | 0.017402 | 289.844 | 0.017736 | 369.941 | 0.017736 | 522.353 | 0.018386 | 634.821 | 0.018851 | 779.259 | 0.018908 | 1023.86 | 0.017559 | 1259.33 | 0.017825 | 1591.35 | 0.017577 | 2231.3 | 0.017789 | 2946.4 | 0.016787 | 4065.7 | 0.01662 | 4790.26 | 0.01657 | 5395.61 | 0.014785 | 5880.17 | 0.018984 | 7371.23 | 0.016438
37.915 | 0.017489 | 68.3982 | 0.018441 | 101.427 | 0.019877 | 117.02 | 0.018221 | 156.232 | 0.021191 | 253.748 | 0.023303 | 330.743 | 0.0223 | 460.514 | 0.023679 | 554.099 | 0.024719 | 689.76 | 0.024037 | 922.736 | 0.021555 | 1131.54 | 0.022122 | 1417.06 | 0.022211 | 1998.88 | 0.022233 | 2660.69 | 0.020524 | 3689.85 | 0.020198 | 4330.08 | 0.020299 | 4901.71 | 0.017968 | 5010.75 | 0.026169 | 6623.24 | 0.020442
35.2458 | 0.020178 | 62.5112 | 0.0221 | 89.6888 | 0.025472 | 105.778 | 0.0223 | 140.66 | 0.026195 | 227.316 | 0.02895 | 288.976 | 0.029212 | 406.809 | 0.030435 | 488.014 | 0.031899 | 634.186 | 0.028377 | 821.673 | 0.027156 | 1019.78 | 0.027237 | 1259.33 | 0.028039 | 1774.62 | 0.028207 | 2388.31 | 0.025498 | 3298.89 | 0.025295 | 3836.59 | 0.025883 | 4417.55 | 0.022056 | 4127.14 | 0.038574 | 5992.96 | 0.024993
32.8301 | 0.023303 | 56.6191 | 0.026725 | 80.0255 | 0.031931 | 95.0445 | 0.027649 | 128.939 | 0.03105 | 204.25 | 0.035931 | 251.224 | 0.038729 | 354.016 | 0.04035 | 436.306 | 0.040028 | 569.833 | 0.03529 | 726.576 | 0.034799 | 924.583 | 0.033069 | 1132.68 | 0.034591 | 1552.06 | 0.03684 | 2178.39 | 0.030649 | 3024.01 | 0.030132 | 3389.17 | 0.033334 | 3914.1 | 0.028123 | 3440.39 | 0.05529 | 5384.83 | 0.031019
30.5494 | 0.026805 | 51.4879 | 0.032349 | 71.4749 | 0.040189 | 85.2293 | 0.034178 | 117.137 | 0.037547 | 182.426 | 0.045358 | 223.038 | 0.049087 | 317.14 | 0.049928 | 380.446 | 0.052804 | 503.883 | 0.045313 | 645.705 | 0.044106 | 849.241 | 0.039079 | 1004.59 | 0.043711 | 1375.18 | 0.047209 | 1975.03 | 0.03736 | 2700.9 | 0.037584 | 3122.35 | 0.039197 | 3613.17 | 0.033069 | 2931.71 | 0.075913 | 4867.52 | 0.038076
28.3988 | 0.03105 | 46.2169 | 0.040028 | 62.7618 | 0.052174 | 76.1988 | 0.042717 | 106.521 | 0.045677 | 158.276 | 0.060255 | 188.546 | 0.068827 | 275.157 | 0.066592 | 336.078 | 0.067127 | 445.565 | 0.057893 | 564.727 | 0.057489 | 760.019 | 0.04855 | 895.465 | 0.054849 | 1235.63 | 0.058125 | 1794.25 | 0.045222 | 2448.77 | 0.04586 | 2876.53 | 0.046274 | 3332.04 | 0.039001 | 2597.59 | 0.096698 | 4360.49 | 0.047636
26.5053 | 0.035751 | 41.6519 | 0.049136 | 55.5535 | 0.066526 | 69.6405 | 0.051141 | 96.2882 | 0.055678 | 142.215 | 0.074559 | 160.829 | 0.094405 | 248.475 | 0.081826 | 289.844 | 0.090522 | 383.118 | 0.078069 | 500.868 | 0.073156 | 684.948 | 0.060075 | 769.963 | 0.073891 | 1122.53 | 0.07071 | 1620.26 | 0.055401 | 2169.69 | 0.058358 | 2647.42 | 0.054794 | 3097.47 | 0.045267 | 2229.07 | 0.13105 | 3851.97 | 0.061044
24.5656 | 0.041454 | 37.9529 | 0.05924 | 50.62 | 0.080286 | 62.2617 | 0.064431 | 85.0591 | 0.071421 | 132.733 | 0.085677 | 140.66 | 0.12305 | 224.156 | 0.099842 | 249.971 | 0.12158 | 327.125 | 0.10676 | 434.564 | 0.096988 | 615.443 | 0.074261 | 666.036 | 0.09875 | 997.59 | 0.089174 | 1470.47 | 0.067464 | 1916.66 | 0.074933 | 2352.75 | 0.069518 | 2805.51 | 0.055345 | 1986.92 | 0.16445 | 3365.53 | 0.080607
22.9277 | 0.047684 | 34.1699 | 0.072791 | 46.0785 | 0.096505 | 53.6964 | 0.086279 | 76.5042 | 0.08811 | 123.389 | 0.098948 | 129.327 | 0.14585 | 196.241 | 0.1304 | 216.23 | 0.16297 | 287.247 | 0.13874 | 383.501 | 0.12416 | 558.549 | 0.08998 | 575.56 | 0.13171 | 893.676 | 0.11134 | 1318.62 | 0.083479 | 1686.38 | 0.096988 | 2111.89 | 0.086366 | 2548.7 | 0.066993 | 1751.7 | 0.21158 | 2943.46 | 0.10549
21.2923 | 0.055179 | 30.4884 | 0.091523 | 42.9633 | 0.1109 | 48.6351 | 0.10496 | 68.2615 | 0.11078 | 116.32 | 0.11179 | 114.13 | 0.1869 | 170.774 | 0.17253 | 189.113 | 0.21306 | 251.978 | 0.17958 | 337.088 | 0.16023 | 476.917 | 0.12342 | 505.396 | 0.17099 | 783.165 | 0.14512 | 1174.2 | 0.10517 | 1494.19 | 0.12367 | 1884.35 | 0.10816 | 2308.47 | 0.081744 | 1524.37 | 0.27911 | 2621.08 | 0.13397
19.833 | 0.063662 | 27.6423 | 0.11145 | 39.7793 | 0.12949 | 43.7436 | 0.1304 | 61.8892 | 0.13464 | 107.807 | 0.12988 | 99.8177 | 0.24362 | 149.956 | 0.22399 | 165.396 | 0.27744 | 221.482 | 0.2329 | 306.845 | 0.19356 | 418.36 | 0.16007 | 438.931 | 0.22692 | 692.524 | 0.18486 | 1069.92 | 0.12731 | 1323.9 | 0.1558 | 1715.29 | 0.13092 | 2114.01 | 0.098159 | 1372.43 | 0.34571 | 2350.4 | 0.1671
18.4367 | 0.073596 | 24.3698 | 0.14382 | 36.9788 | 0.14984 | 37.9909 | 0.17271 | 55.6091 | 0.1676 | 99.9176 | 0.15105 | 88.3535 | 0.31218 | 129.327 | 0.30084 | 140.941 | 0.38437 | 200.205 | 0.28589 | 285.529 | 0.22376 | 357.217 | 0.21933 | 374.781 | 0.3097 | 589.54 | 0.25585 | 958.474 | 0.15911 | 1183.63 | 0.19337 | 1570.8 | 0.15768 | 1845.19 | 0.12936 | 1243.07 | 0.42267 | 2076.29 | 0.21499
17.1903 | 0.08474 | 21.6357 | 0.18265 | 33.393 | 0.1843 | 33.7623 | 0.21715 | 50.4179 | 0.20369 | 90.9533 | 0.18284 | 75.8188 | 0.42225 | 113.221 | 0.39213 | 123.76 | 0.50049 | 176.151 | 0.36856 | 261.215 | 0.26549 | 320.007 | 0.27194 | 332.069 | 0.40206 | 515.606 | 0.33583 | 862.938 | 0.19727 | 1080.67 | 0.2315 | 1451.48 | 0.18709 | 1631.64 | 0.16511 | 1153.25 | 0.49403 | 1869.34 | 0.26682
15.9641 | 0.098061 | 19.324 | 0.22715 | 30.3667 | 0.22265 | 30.1247 | 0.27303 | 45.2113 | 0.2533 | 83.8765 | 0.21521 | 67.3798 | 0.53517 | 103.063 | 0.47324 | 113.448 | 0.601 | 156.701 | 0.46853 | 239.21 | 0.31532 | 283.254 | 0.34848 | 300.469 | 0.498 | 442.9 | 0.45287 | 767.657 | 0.25229 | 974.908 | 0.28732 | 1352 | 0.21911 | 1489.71 | 0.19846 | 1069.92 | 0.57859 | 1633.27 | 0.35128
14.8254 | 0.11359 | 17.4676 | 0.27688 | 27.8643 | 0.26443 | 26.5584 | 0.35234 | 40.8271 | 0.31156 | 77.1959 | 0.25381 | 60.5425 | 0.66687 | 93.5359 | 0.57801 | 102.857 | 0.73627 | 143.358 | 0.56149 | 222.815 | 0.36343 | 257.069 | 0.42394 | 274.059 | 0.61008 | 396.368 | 0.56318 | 693.911 | 0.31156 | 898.155 | 0.34261 | 1265.65 | 0.25585 | 1362.86 | 0.23689 | 986.677 | 0.68649 | 1466.07 | 0.43816
13.713 | 0.1325 | 16.3356 | 0.31501 | 25.2631 | 0.32298 | 23.8395 | 0.43598 | 36.9419 | 0.37978 | 71.8331 | 0.29342 | 54.4534 | 0.83597 | 84.6348 | 0.71308 | 94.3816 | 0.88589 | 131.413 | 0.67492 | 206.922 | 0.42183 | 235.649 | 0.51009 | 255.531 | 0.71308 | 370.311 | 0.64522 | 613.6 | 0.40529 | 830.762 | 0.40367 | 1196.72 | 0.29312 | 1274.54 | 0.2714 | 913.554 | 0.81127 | 1312.04 | 0.55092
12.7859 | 0.15196 | 15.2008 | 0.36307 | 22.8819 | 0.39449 | 20.3554 | 0.59562 | 34.5479 | 0.43729 | 66.3103 | 0.34571 | 50.0662 | 1.0049 | 78.1278 | 0.84184 | 86.8642 | 1.0627 | 119.742 | 0.8227 | 192.933 | 0.48814 | 218.622 | 0.5992 | 241.373 | 0.81533 | 344.931 | 0.74814 | 543.67 | 0.52721 | 791.036 | 0.44791 | 1131.54 | 0.33583 | 1186 | 0.31406 | 845.851 | 0.96064 | 1188.37 | 0.67425
11.8384 | 0.1769 | 14.0883 | 0.42267 | 20.829 | 0.47371 | 17.3804 | 0.81533 | 32.4385 | 0.49949 | 60.0601 | 0.42098 | 46.9154 | 1.1698 | 71.8331 | 1.0119 | 80.9107 | 1.2484 | 108.564 | 1.0119 | 181.697 | 0.55368 | 203.842 | 0.70176 | 226.183 | 0.94633 | 323.223 | 0.85885 | 487.526 | 0.66821 | 740.513 | 0.51677 | 1069.92 | 0.38706 | 1109.14 | 0.35982 | 778.48 | 1.1524 | 1103.61 | 0.7818
10.9501 | 0.20697 | 13.0442 | 0.49403 | 18.7528 | 0.58792 | 16.1892 | 0.93973 | 30.2455 | 0.58265 | 55.8319 | 0.48667 | 44.2275 | 1.3496 | 67.6499 | 1.1605 | 75.2899 | 1.4738 | 100.017 | 1.2163 | 169.923 | 0.63625 | 191.204 | 0.80964 | 214.507 | 1.0756 | 302.882 | 0.98594 | 460.975 | 0.75793 | 690.45 | 0.60401 | 1010.64 | 0.45016 | 1040.38 | 0.41141 | 709.346 | 1.4231 | 1027.97 | 0.90289
10.2098 | 0.23831 | 12.2478 | 0.56318 | 17.1046 | 0.7074 | 15.277 | 1.0564 | 28.2007 | 0.67695 | 50.7213 | 0.58792 | 41.4856 | 1.5822 | 63.0764 | 1.3646 | 70.3404 | 1.7364 | 92.0513 | 1.4767 | 159.388 | 0.7304 | 178.1 | 0.95776 | 205.684 | 1.1887 | 283.821 | 1.1364 | 424.259 | 0.91196 | 647.645 | 0.69408 | 955.603 | 0.52301 | 958.474 | 0.49206 | 661.39 | 1.6767 | 947.041 | 1.0659
9.406 | 0.28107 | 11.3742 | 0.65826 | 15.7895 | 0.82848 | 14.4594 | 1.1839 | 26.4524 | 0.78024 | 47.2922 | 0.68034 | 39.4229 | 1.8019 | 59.2251 | 1.587 | 66.5096 | 2.0054 | 85.828 | 1.7451 | 150.256 | 0.83264 | 165.396 | 1.1501 | 196.045 | 1.3429 | 266.758 | 1.3071 | 390.858 | 1.1061 | 611.762 | 0.78887 | 909.907 | 0.5992 | 906.275 | 0.55258 | 612.374 | 2.0276 | 871.611 | 1.2812
8.6915 | 0.32885 | 10.6904 | 0.7474 | 14.7515 | 0.95489 | 13.8786 | 1.3006 | 24.8125 | 0.90108 | 43.6562 | 0.80319 | 37.2759 | 2.0768 | 55.2764 | 1.8905 | 62.699 | 2.3299 | 81.6422 | 1.9815 | 142.358 | 0.9435 | 155.608 | 1.3429 | 186.297 | 1.5355 | 250.972 | 1.5066 | 368.464 | 1.2761 | 576.712 | 0.89928 | 868.131 | 0.68649 | 840.791 | 0.64651 | 565.858 | 2.474 | 813.498 | 1.4976
7.9038 | 0.39213 | 10.0276 | 0.85799 | 13.7267 | 1.105 | 13.3344 | 1.4231 | 23.2975 | 1.0375 | 40.5018 | 0.9435 | 35.1754 | 2.4543 | 52.4755 | 2.1573 | 59.5816 | 2.6881 | 77.1959 | 2.2861 | 134.739 | 1.0756 | 147.428 | 1.5432 | 177.744 | 1.7417 | 236.593 | 1.7364 | 344.931 | 1.5217 | 541.5 | 1.0344 | 827.445 | 0.78887 | 771.505 | 0.77634 | 528.659 | 2.9827 | 750.202 | 1.8091
7.2525 | 0.46294 | 9.4437 | 0.97418 | 12.9144 | 1.2609 | 12.8757 | 1.5509 | 22.117 | 1.1675 | 38.1813 | 1.0723 | 33.4933 | 2.8175 | 49.1239 | 2.5724 | 55.6091 | 3.2636 | 73.9468 | 2.575 | 126.893 | 1.2409 | 139.678 | 1.7965 | 169.753 | 1.9815 | 223.932 | 1.9974 | 324.843 | 1.7983 | 508.438 | 1.203 | 787.878 | 0.91196 | 709.346 | 0.92945 | 493.411 | 3.6286 | 698.785 | 2.153
6.6615 | 0.54708 | 8.876 | 1.1116 | 12.1017 | 1.4577 | 12.4205 | 1.6953 | 20.829 | 1.3349 | 35.6 | 1.2584 | 31.9556 | 3.2669 | 46.5416 | 2.9798 | 53.0559 | 3.7391 | 70.8345 | 2.8917 | 119.264 | 1.4461 | 132.999 | 2.0623 | 160.829 | 2.3183 | 212.585 | 2.2838 | 309.619 | 2.0562 | 478.829 | 1.3852 | 751.704 | 1.0564 | 661.39 | 1.081 | 461.436 | 4.4143 | 651.543 | 2.575
6.1617 | 0.63816 | 8.2594 | 1.2928 | 11.4198 | 1.6717 | 12.0413 | 1.842 | 19.8131 | 1.5051 | 33.6612 | 1.4345 | 30.6106 | 3.7842 | 44.4047 | 3.4344 | 50.2166 | 4.472 | 67.7853 | 3.2604 | 112.995 | 1.6667 | 127.401 | 2.3557 | 153.906 | 2.6402 | 200.606 | 2.6507 | 294.225 | 2.3961 | 456.845 | 1.5509 | 717.909 | 1.2335 | 617.91 | 1.2609 | 434.13 | 5.3433 | 608.711 | 3.1076
5.7509 | 0.73333 | 7.8096 | 1.4591 | 10.8411 | 1.8886 | 11.7206 | 1.9894 | 18.7716 | 1.7174 | 31.6692 | 1.6617 | 29.4103 | 4.3922 | 42.4508 | 3.9387 | 48.007 | 5.2743 | 64.9973 | 3.6871 | 105.25 | 1.9954 | 122.406 | 2.6881 | 146.254 | 3.0859 | 191.396 | 3.0248 | 279.595 | 2.8203 | 435.434 | 1.7556 | 682.214 | 1.4621 | 576.136 | 1.4797 | 416.274 | 6.1524 | 572.117 | 3.7204
5.3567 | 0.8503 | 7.4734 | 1.611 | 10.3537 | 2.123 | 11.4426 | 2.1486 | 17.9098 | 1.9384 | 30.1247 | 1.8829 | 28.3988 | 5.0422 | 40.6641 | 4.5215 | 45.8028 | 6.2641 | 62.324 | 4.2032 | 100.217 | 2.2952 | 117.137 | 3.1451 | 141.082 | 3.4933 | 182.426 | 3.4689 | 267.025 | 3.3262 | 413.784 | 2.0014 | 658.091 | 1.6584 | 532.905 | 1.784 | 402.358 | 7.0065 | 543.127 | 4.3529
5.0146 | 0.97808 | 7.1804 | 1.7697 | 9.9677 | 2.3463 | 11.1378 | 2.3557 | 17.0193 | 2.2008 | 28.5411 | 2.1551 | 27.4769 | 5.9408 | 39.4623 | 5.012 | 44.3604 | 7.2344 | 59.8204 | 4.8348 | 95.6165 | 2.6375 | 112.319 | 3.7279 | 135.415 | 4.0222 | 175.448 | 3.9073 | 256.555 | 3.8607 | 397.957 | 2.2163 | 632.919 | 1.9076 | 499.868 | 2.0893 | 389.687 | 8.0837 | 512.522 | 5.322
4.732 | 1.1161 | 6.8713 | 1.9696 | 9.6731 | 2.5596 | 10.8519 | 2.5853 | 16.3029 | 2.4617 | 27.0678 | 2.4839 | 26.6116 | 6.9646 | 38.296 | 5.6398 | 43.1786 | 8.3716 | 57.1881 | 5.6341 | 91.3178 | 3.0369 | 108.347 | 4.4275 | 130.365 | 4.6406 | 170.263 | 4.2924 | 246.495 | 4.5533 | 383.501 | 2.4518 | 610.54 | 2.1964 | 469.817 | 2.4421 | 377.414 | 9.6008 | 488.991 | 6.4163
4.4564 | 1.2864 | 6.5624 | 2.2386 | 9.3685 | 2.8259 | 10.5734 | 2.9004 | 15.648 | 2.726 | 25.4406 | 2.9442 | 25.9027 | 8.1323 | 37.2014 | 6.3018 | 42.2391 | 9.7167 | 55.2764 | 6.4614 | 87.0381 | 3.5567 | 104.83 | 5.2585 | 125.882 | 5.3701 | 165.893 | 4.7013 | 235.178 | 5.6341 | 368.464 | 2.7452 | 591.312 | 2.4839 | 446.904 | 2.7866 | 366.26 | 11.5981 | 469.347 | 7.9078
4.2095 | 1.4723 | 6.3684 | 2.4592 | 9.0916 | 3.1231 | 10.3021 | 3.2539 | 15.1704 | 2.959 | 24.0551 | 3.4689 | 25.2379 | 9.9627 | 36.1019 | 7.1839 | 41.4027 | 11.9992 | 53.5891 | 7.3658 | 83.8765 | 4.0749 | 101.529 | 6.2454 | 122.283 | 6.1956 | 161.959 | 5.1287 | 227.544 | 6.6848 | 355.08 | 3.0766 | 569.833 | 2.9033 | 425.533 | 3.2054 | 357.932 | 13.8855 | 453.204 | 9.7361
3.9604 | 1.7072 | 6.1248 | 2.8006 | 8.8671 | 3.4207 | 10.088 | 3.6322 | 14.7958 | 3.1514 | 22.8362 | 4.083 | 24.7877 | 12.1562 | 35.2811 | 8.1567 | 40.7048 | 14.1094 | 52.266 | 8.3968 | 80.9107 | 4.7013 | 98.43 | 7.6817 | 119.742 | 7.0206 | 158.435 | 5.6229 | 219.937 | 8.0594 | 341.498 | 3.4793 | 548.585 | 3.4104 | 403.164 | 3.7353 | 349.794 | 16.8415 | 439.371 | 12.2784
3.7447 | 1.9676 | 5.8847 | 3.2997 | 8.6051 | 3.8376 | 9.8193 | 4.2242 | 14.3442 | 3.4551 | 21.7877 | 4.7819 | 24.2483 | 15.254 | 34.5133 | 9.2151 | 40.0587 | 17.4239 | 51.2311 | 9.6489 | 78.3625 | 5.4622 | 96.0958 | 9.1325 | 116.32 | 8.3298 | 154.06 | 6.3145 | 214.507 | 9.4863 | 330.413 | 3.8839 | 530.778 | 3.9229 | 386.195 | 4.2795 | 342.524 | 20.8602 | 425.959 | 15.9561
3.5443 | 2.2724 | 5.7222 | 3.7428 | 8.3674 | 4.2795 | 9.5005 | 5.0827 | 13.9063 | 3.8223 | 21.0804 | 5.4567 | 23.8634 | 19.4305 | 33.6612 | 10.89 | 39.4623 | 21.474 | 50.2166 | 11.2104 | 75.8946 | 6.3716 | 93.7232 | 10.9336 | 114.588 | 9.4295 | 150.557 | 7.1053 | 209.002 | 11.4254 | 319.687 | 4.3442 | 515.091 | 4.4631 | 370.681 | 4.9128 | 337.425 | 27.1899 | 415.858 | 20.0022
3.3748 | 2.6218 | 5.5642 | 4.3312 | 8.1364 | 4.859 | 9.2752 | 5.9945 | 13.5494 | 4.1864 | 20.5189 | 6.1278 | 23.5081 | 25.3263 | 33.1601 | 12.5641 | 38.9916 | 26.2547 | 49.2715 | 12.9208 | 74.169 | 7.2127 | 91.5006 | 13.4347 | 112.656 | 11.0656 | 147.281 | 8.0433 | 205.273 | 13.0899 | 311.171 | 4.7963 | 499.368 | 5.1338 | 355.791 | 5.6285 | 332.401 | 33.5772 | 408.439 | 24.9493
3.2231 | 3.0067 | 5.4214 | 4.9523 | 7.9038 | 5.668 | 9.0191 | 7.2706 | 13.2281 | 4.6036 | 19.8727 | 7.1409 | 23.3208 | 30.2001 | 32.7645 | 14.8923 | 38.5265 | 32.4547 | 48.6351 | 14.9072 | 72.4101 | 8.2966 | 89.5096 | 16.8078 | 110.979 | 12.8693 | 142.928 | 9.6779 | 201.41 | 15.1022 | 304.096 | 5.3326 | 483.158 | 5.9586 | 344.586 | 6.4873 | 326.145 | 43.4603 | 400.352 | 32.2283
3.1185 | 3.3664 | 5.277 | 5.7825 | 7.6856 | 6.6449 | 8.7877 | 8.6525 | 12.85 | 5.201 | 19.2468 | 8.422 | 23.1581 | 39.3245 | 32.3413 | 18.0445 | 38.0289 | 41.4234 | 48.007 | 17.2505 | 70.8345 | 9.6973 | 87.4744 | 21.6033 | 109.546 | 15.1628 | 139.958 | 11.1768 | 197.422 | 17.7581 | 297.479 | 5.9527 | 467.941 | 6.8884 | 332.069 | 7.7357 | 320.327 | 57.8497 | 393.21 | 40.4816
3.0354 | 3.7056 | 5.1467 | 6.7385 | 7.5033 | 7.79 | 8.5793 | 10.7708 | 12.5202 | 5.8524 | 18.7154 | 10.174 | 23.0426 | 50.8484 | 32.0195 | 21.9517 | 37.5377 | 55.5814 | 47.4818 | 19.8032 | 69.5709 | 11.1545 | 85.7423 | 27.7947 | 108.239 | 17.4937 | 137.324 | 12.9208 | 194.677 | 20.6733 | 290.715 | 6.752 | 453.204 | 7.9315 | 321.611 | 9.3919 | 313.044 | 78.8738 | 385.424 | 51.6685
2.9575 | 4.1365 | 5.0347 | 7.7357 | 7.3327 | 9.0961 | 8.4094 | 12.9597 | 12.2233 | 6.6648 | 18.1804 | 12.7795 | 22.859 | 67.279 | 31.6376 | 27.2171 | 37.1271 | 72.2295 | 47.0093 | 22.9391 | 68.4666 | 12.7923 | 84.297 | 34.1529 | 106.948 | 20.7354 | 135.009 | 14.9072 | 190.632 | 25.2252 | 284.958 | 7.5977 | 440.25 | 9.1783 | 311.794 | 11.6329 | 306.845 | 104.047 | 378.548 | 64.5764
2.8874 | 4.6452 | 4.935 | 8.9966 | 7.1875 | 10.6211 | 8.2676 | 15.3152 | 11.9813 | 7.3879 | 17.6608 | 16.8921 | 22.6542 | 87.7814 | 31.229 | 34.5997 | 36.7944 | 92.9303 | 46.4486 | 26.5717 | 67.2452 | 15.1779 | 82.876 | 43.3301 | 105.778 | 25.8121 | 132.866 | 17.2333 | 188.169 | 29.8697 | 279.316 | 8.5749 | 425.108 | 10.6211 | 300.469 | 15.6715 | 301.07 | 139.47 | 372.167 | 80.2261
2.8133 | 5.2585 | 4.8373 | 10.3588 | 7.0311 | 12.665 | 8.1364 | 18.0445 | 11.7206 | 8.3884 | 17.2592 | 21.7768 | 22.4288 | 123.698 | 30.8565 | 45.3245 | 36.4648 | 121.249 | 45.9864 | 31.3385 | 65.9137 | 18.8186 | 81.5606 | 53.7234 | 104.516 | 32.1639 | 130.757 | 20.1226 | 185.739 | 35.2987 | 273.511 | 9.8932 | 411.308 | 12.377 | 292.464 | 20.3045 | 295.109 | 187.326 | 364.433 | 102.396
2.7576 | 5.8641 | 4.751 | 12.0353 | 6.8302 | 16.1649 | 8.0233 | 21.3883 | 11.4885 | 9.6296 | 16.9344 | 28.413 | 22.2501 | 165.48 | 30.6106 | 57.4462 | 36.1742 | 156.624 | 45.4379 | 39.4032 | 64.9973 | 22.8476 | 80.5071 | 66.2774 | 102.96 | 40.4411 | 128.296 | 24.5287 | 182.608 | 41.8398 | 268.632 | 11.2779 | 397.559 | 14.3801 | 287.247 | 25.2757 | 289.554 | 249.099 | 357.574 | 133.199
2.6895 | 6.7453 | 4.6616 | 14.337 | 6.6749 | 19.7834 | 7.9197 | 25.4533 | 11.261 | 11.0435 | 16.5493 | 40.4411 | 22.0507 | 224.27 | 30.3363 | 73.7624 | 36.0658 | 208.69 | 44.9408 | 49.0994 | 64.0296 | 27.9061 | 79.4673 | 82.5867 | 101.732 | 49.8415 | 126.386 | 28.8712 | 180.069 | 49.8415 | 262.524 | 13.4213 | 382.353 | 17.2333 | 283.821 | 31.8121 | 284.105 | 328.932 | 350.144 | 175.888
2.6178 | 7.8605 | 4.5784 | 16.9428 | 6.5558 | 23.9231 | 7.8409 | 29.4839 | 11.049 | 12.7667 | 16.2704 | 55.86 | 21.9627 | 269.037 | 30.0045 | 101.783 | 35.9219 | 265.297 | 44.6273 | 60.4519 | 63.2026 | 34.4272 | 78.2842 | 106.043 | 100.619 | 60.1504 | 124.38 | 35.2634 | 176.857 | 60.8157 | 256.555 | 15.829 | 370.311 | 20.3452 | 279.037 | 41.3407 | 279.316 | 419.411 | 342.867 | 230.869
2.5583 | 8.9966 | 4.4877 | 20.7562 | 6.4453 | 28.987 | 7.7628 | 33.9486 | 10.8628 | 14.7294 | 16.0602 | 74.9521 | 21.8969 | 298.524 | 29.7952 | 130.954 | 35.8501 | 299.122 | 44.2717 | 74.6529 | 62.4487 | 42.0916 | 77.3504 | 133.333 | 99.3199 | 73.984 | 122.528 | 42.5146 | 173.876 | 73.5414 | 252.483 | 18.4091 | 358.29 | 24.4064 | 274.059 | 53.7234 | 274.882 | 520.013 | 338.439 | 285.388
2.5127 | 10.1842 | 4.4033 | 25.1245 | 6.3557 | 33.0442 | 7.701 | 39.7197 | 10.7118 | 17.0789 | 15.8053 | 104.673 |  |  | 29.6762 | 184.352 |  |  | 44.0509 | 87.9571 | 61.7038 | 53.402 | 76.4278 | 172.751 | 98.0371 | 93.7704 | 120.222 | 52.5018 | 171.459 | 89.019 | 247.483 | 21.5817 | 350.494 | 27.6008 | 269.17 | 70.6578 | 271.875 | 599.954 | 331.737 | 369.39
2.4678 | 11.5634 | 4.3247 | 30.0796 | 6.2799 | 38.1241 | 7.6244 | 45.0533 | 10.5734 | 19.6062 | 15.648 | 141.719 |  |  | 29.6466 | 232.026 |  |  | 43.6562 | 110.261 | 60.846 | 67.8873 | 75.5917 | 218.733 | 96.481 | 121.735 | 118.669 | 65.4213 | 169.244 | 104.883 | 242.34 | 26.0195 | 340.475 | 32.4872 | 264.898 | 89.5547 |  |  | 326.472 | 459.828
2.4141 | 13.6105 | 4.2646 | 35.1578 | 6.2174 | 43.7218 | 7.5636 | 51.1544 | 10.4369 | 22.6202 | 15.5544 | 184.721 |  |  | 29.6169 | 271.741 |  |  | 43.4385 | 139.609 | 60.1804 | 88.398 | 75.1395 | 269.576 | 95.0445 | 157.095 | 116.786 | 85.614 | 167.728 | 123.328 | 236.83 | 32.1639 | 330.083 | 39.839 | 260.693 | 110.924 |  |  | 321.933 | 542.318
2.383 | 15.6715 | 4.2137 | 40.9703 | 6.174 | 49.9413 | 7.5184 | 57.7341 | 10.3227 | 26.0716 | 15.5078 | 234.358 |  |  | 29.6169 | 297.928 |  |  | 43.2651 | 166.143 | 59.522 | 111.592 | 74.7647 | 298.524 | 93.7232 | 196.144 | 114.817 | 114.875 | 165.727 | 146.767 | 232.141 | 39.68 | 321.29 | 46.9859 | 257.583 | 131.742 |  |  | 319.687 | 599.954
2.3451 | 18.4644 | 4.1676 | 48.6109 | 6.1187 | 57.8497 | 7.4659 | 64.965 | 10.1996 | 30.1097 | 15.4459 | 268.5 | [6 empty] | 43.0924 | 210.998 | 58.9887 | 147.946 |  |  | 92.7906 | 234.592 | 113.448 | 145.307 | 163.75 | 176.947 | 227.544 | 48.5623 | 312.731 | 55.0834 | 254.256 | 157.252
2.3125 | 21.3029 | 4.1179 | 59.2549 | 6.076 | 67.2118 | 7.4064 | 73.7624 | 10.1183 | 34.8428 | 15.4305 | 298.524 | [6 empty] | 43.0063 | 260.564 | 58.4018 | 194.581 |  |  | 92.0513 | 264.502 | 112.656 | 172.405 | 161.797 | 212.268 | 223.261 | 59.7906 | 305.315 | 63.2344 | 250.722 | 193.998
2.2872 | 24.4553 | 4.0851 | 70.6578 | 6.0457 | 78.8738 | 7.3401 | 87.2563 | 10.0779 | 40.1992 | [8 empty] | 42.9633 | 299.122 | 58.1105 | 247.114 |  |  | 91.1353 | 299.721 | 112.094 | 201.311 | 160.347 | 246.374 | 219.059 | 75.6297 | 296.588 | 73.3945 | 246.989 | 248.353
2.2532 | 29.1322 | 4.0526 | 84.7622 | 6.0095 | 93.2095 | 7.2962 | 99.7682 | 10.0578 | 46.5649 | [10 empty] | 57.9944 | 275.022 |  |  |  |  | 111.647 | 231.563 | 159.229 | 278.899 | 214.507 | 97.7927 | 288.976 | 83.9188 | 241.614 | 324.684
2.2308 | 34.2555 | 4.0203 | 101.58 | 5.9796 | 112.488 | 7.2525 | 114.76 | 10.0176 | 54.2633 | [10 empty] | 57.8207 | 299.721 |  |  |  |  | 111.201 | 263.447 | 158.593 | 299.122 | 211.737 | 116.845 | 280.997 | 96.7228 | 238.255 | 413.167
2.2064 | 39.7594 | 4.0082 | 124.443 | 5.9676 | 131.874 | 7.2236 | 131.085 | 9.9876 | 64.3829 | [16 empty] | 110.536 | 299.721 |  |  | 208.376 | 141.719 | 272.965 | 111.48 | 234.005 | 535.314
2.1888 | 46.5649 | 4.0042 | 147.65 | 5.9676 | 157.409 | 7.2019 | 151.086 | 9.9777 | 77.933 | [20 empty] | 204.659 | 178.546 | 264.898 | 127.849 | 232.373 | 598.755
2.1735 | 53.1888 | 3.9922 | 172.405 | 5.9676 | 194.776 | 7.1875 | 175.712 | 9.9777 | 92.8374 | [20 empty] | 202.42 | 214.401 | 257.841 | 143.574
2.1584 | 61.3655 | 3.9882 | 205.172 | 5.9617 | 238.376 | 7.1589 | 200.708 | 9.9577 | 111.146 | [20 empty] | 200.807 | 246.128 | 250.221 | 162.041
2.1347 | 75.4031 | 3.9842 | 249.348 | 5.9617 | 268.232 | 7.1445 | 229.717 | 9.9577 | 139.33 | [20 empty] | 199.207 | 282.831 | 243.799 | 182.701
2.1156 | 88.1332 | 3.9803 | 298.226 | 5.9557 | 297.928 | 7.1231 | 260.044 | 9.9577 | 172.233 | [20 empty] | 197.817 | 329.591 | 238.494 | 204.149
2.1051 | 102.498 |  |  |  |  | 7.1231 | 281.702 | 9.9777 | 211.844 | [20 empty] | 196.437 | 381.401 | 234.708 | 223.374
2.082 | 122.223 |  |  |  |  | 7.1231 | 302.733 | 9.9577 | 249.598 | [20 empty] | 194.872 | 439.594 | 232.605 | 242.463
2.0654 | 142.715 | [6 empty] | 9.9677 | 299.721 | [20 empty] | 193.126 | 523.142 | 230.061 | 267.696
2.049 | 168.991 | [28 empty] | 191.587 | 600.554 | 226.862 | 300.321
2.0347 | 194.387 | [30 empty] | 224.38 | 336.922
2.0185 | 226.524 | [30 empty] | 222.148 | 377.606
2.0044 | 259.524 | [30 empty] | 219.937 | 429.599
1.9924 | 301.223 | [30 empty] | 218.622 | 470.056
[32 empty] | 217.531 | 516.902
[32 empty] | 217.097 | 561.074
[32 empty] | 216.446 | 600.554